## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 55 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.2 | 9680 | 42.06 | 3872.7 | 720 | 7335.5 | 6615.5 | 10.1 | 84.1057 | 7226.5 | 0 | 139 | 30 |  | 76.5683 | 6615.5
2 | 0 | 635 | 635 | 0 | 0 | 4 | 635 | 55 | 0 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.25 | 9800 | 41.89 | 3673.8 | 120 | 6533.5 | 6413.5 | 10.1 | 84.0085 | 6502.5 | 0 | 31 | 0 |  | 74.2303 | 6413.5
3 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.1 | 9440 | 42.1 | 3919.5 | -360 | 6356.5 | 6716.5 | 10.1 | 84.3008 | 6387.5 | 0 | 29 | 60 |  | 77.7373 | 6716.5
4 | 0 | 690 | 690 | 0 | 0 | 4 | 690 | 55 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.1 | 9440 | 42.03 | 3837.6 | 0 | 6969 | 6969 | 10.1 | 84.3008 | 6874.6 | 0 | 94.4 | 0 |  | 80.6597 | 6969
5 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 85.2 | 9680 | 42.05 | 3861 | 240 | 6956.5 | 6716.5 | 10.1 | 84.1057 | 6874.6 | 0 | 81.9 | 0 |  | 77.7373 | 6716.5
6 | 0 | 645 | 645 | 0 | 0 | 4 | 645 | 55 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.95 | 9080 | 41.95 | 3744 | -600 | 5914.5 | 6514.5 | 10.1 | 84.5953 | 5357.6 | 0 | 556.9 | 0 |  | 75.3993 | 6514.5
7 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 55 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.9 | 8960 | 42.05 | 3861 | -120 | 6546 | 6666 | 10.1 | 84.6939 | 6195 | 0 | 351 | 0 |  | 77.1528 | 6666
8 | 105 | 250 | 355 | 0 | 0 | 4 | 355 | 70 | 2.8 | 6.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.9 | 8960 | 41.8 | 3568.5 | 0 | 3585.5 | 3585.5 | 10.1 | 84.6939 | 3367.3 | 0 | 218.2 | 0 |  | 41.4988 | 3585.5
9 | 260 | 85 | 345 | 0 | 0 | 3 | 345 | 70 | 6.95 | 2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.65 | 5960 | 41.78 | 3545.1 | -3000 | 5285.5753 | 3484.5 | 10.1 | 87.2357 | 5367.6 | 4801.0753 | 17.9753 | 100 |  | 40.3299 | 3484.5
10 | 55 | 415 | 470 | 0 | 0 | 4 | 470 | 109 | 1.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 41.97 | 3767.4 | 360 | 5107 | 4747 | 10.1 | 86.9226 | 5058.9 | 0 | 108.1 | 60 |  | 54.9421 | 4747
11 | 380 | 0 | 380 | 0 | 0 | 3 | 380 | 54 | 8.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.6 | 8240 | 41.72 | 3474.9 | 1920 | 6194.1702 | 3838 | 10.1 | 85.2903 | 6119.8 | 436.1702 | 74.3702 | 0 |  | 44.4213 | 3838
12 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 55 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.65 | 8360 | 41.89 | 3673.8 | 120 | 4362 | 4242 | 10.1 | 85.1903 | 4239.05 | 0 | 122.95 | 0 |  | 49.0972 | 4242
13 | 340 | 70 | 410 | 0 | 0 | 3 | 410 | 80 | 8.7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.55 | 8120 | 41.76 | 3521.7 | -240 | 3901 | 4141 | 10.1 | 85.3905 | 3951.6 | 0 | 9.4 | 60 |  | 47.9282 | 4141
14 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 40 | 0 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.55 | 8120 | 41.96 | 3755.7 | 0 | 4595.5 | 4595.5 | 10.1 | 85.3905 | 4591.7 | 0 | 63.8 | 60 |  | 53.1887 | 4595.5
15 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 40 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.75 | 8600 | 41.93 | 3720.6 | 480 | 4924 | 4444 | 10.1 | 84.991 | 4943.2 | 0 | 40.8 | 60 |  | 51.4352 | 4444
16 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 40 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.8 | 8720 | 41.07 | 2714.4 | 120 | 3958 | 3838 | 10.1 | 84.8917 | 3959 | 0 | 59 | 60 |  | 44.4213 | 3838
17 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 55 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.8 | 8720 | 41.42 | 3123.9 | 0 | 4305 | 4305 | 10.5 | 81.6578 | 4126.8 | 0 | 178.2 | 0 |  | 49.8264 | 4305
18 | 0 | 480 | 480 | 0 | 0 | 3 | 480 | 45 | 0 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000 | 41.98 | 3779.1 | -720 | 4032 | 4752 | 9.9 | 87.2181 | 3877.5 | 0 | 184.5 | 30 |  | 55 | 4752
19 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.63 | 8312 | 41.52 | 3240.9 | 312 | 4503.5 | 4191.5 | 10.1 | 85.2303 | 4530 | 0 | 73.5 | 100 |  | 48.5127 | 4191.5
20 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 45 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.7 | 8480 | 42.02 | 3825.9 | 168 | 4612 | 4444 | 10.1 | 85.0905 | 4522.5 | 0 | 89.5 | 0 |  | 51.4352 | 4444
21 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 55 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.6 | 8240 | 41.82 | 3591.9 | -240 | 4658.5 | 4898.5 | 10.1 | 85.2903 | 4605 | 0 | 93.5 | 40 |  | 56.6956 | 4898.5
22 | 0 | 400 | 400 | 0 | 0 | 3 | 400 | 40 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.5 | 8000 | 41.89 | 3673.8 | -240 | 3800 | 4040 | 10.1 | 85.491 | 3772.5 | 0 | 87.5 | 60 |  | 46.7593 | 4040
23 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 40 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.36 | 7664 | 41.88 | 3662.1 | -336 | 4075.0426 | 3927 | 10.2 | 84.9326 | 4117.5 | 484.0426 | 57.5426 | 100 |  | 45.4514 | 3927
24 | 0 | 365 | 365 | 0 | 0 | 4 | 365 | 40 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.47 | 7928 | 41.76 | 3521.7 | 264 | 4060 | 3796 | 10.4 | 83.0835 | 4033 | 0 | 87 | 60 |  | 43.9352 | 3796
25 | 85 | 480 | 565 | 0 | 0 | 3 | 565 | 95 | 1.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.6 | 8240 | 41.55 | 3276 | 312 | 6018.5 | 5706.5 | 10.1 | 85.2903 | 5905.7 | 0 | 172.8 | 60 |  | 66.0475 | 5706.5
26 | 0 | 393 | 393 | 0 | 0 | 4 | 393 | 54 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8240 | 41.66 | 3404.7 | 0 | 3969.3 | 3969.3 | 10.1 | 85.2903 | 3944.2 | 0 | 85.1 | 60 |  | 45.941 | 3969.3
27 | 465 | 32 | 497 | 0 | 0 | 3 | 497 | 75 | 11.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.8 | 8720 | 41.85 | 3627 | 480 | 5499.7 | 5019.7 | 10.1 | 84.8917 | 5321.7 | 0 | 178 | 0 |  | 58.0984 | 5019.7
28 | 0 | 395 | 395 | 0 | 0 | 4 | 395 | 40 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.9 | 8960 | 41.65 | 3393 | 240 | 4229.5 | 3989.5 | 10.1 | 84.6939 | 4102.6 | 0 | 126.9 | 0 |  | 46.1748 | 3989.5
29 | 390 | 0 | 390 | 0 | 0 | 3 | 390 | 40 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.05 | 9320 | 41.75 | 3510 | 360 | 4455 | 4095 | 10.5 | 81.1836 | 4270.5 | 0 | 184.5 | 0 |  | 47.3958 | 4095
30 | 0 | 385 | 385 | 0 | 0 | 4 | 385 | 40 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.35 | 10040 | 41.9 | 3685.5 | 720 | 4608.5 | 3888.5 | 10.1 | 83.8147 | 4518.7 | 0 | 89.8 | 0 |  | 45.0058 | 3888.5
31 | 505 | 320 | 825 | 0 | 0 | 4 | 825 | 80 | 10.75 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 85.1 | 9440 | 42.1 | 3919.5 | -600 | 7732.5 | 8332.5 | 10.1 | 84.3008 | 7645.19 | 0 | 87.31 | 0 |  | 96.441 | 8332.5
| 7365 | 7735 | 15100 | 0 | 0 | 109 | 14991 | 109 | 164.45 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 34 |  |  | 84.739 | 8573.6774 | 41.831 | 3604.7323 | 480 | 159083.288 | 152882 | 10.1246 | 84.806 | 156309.84 | 5721.288 | 3773.448 | 1000 |  | 57.0796 | 152882