## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 260 | 0 | 260 | 0 | 0 | 4 | 260 | 40 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200 | 41.9 | 3685.5 | -120 | 2506 | 2626 | 10.1 | 84.4969 | 2385.8 | 0 | 120.2 | 0 |  | 30.3935 | 2626
2 | 100 | 133 | 233 | 0 | 0 | 3 | 233 | 54 | 2.1 | 2.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 85.05 | 9320 | 41.65 | 3393 | 120 | 2543.2 | 2423.2 | 10.4 | 81.9642 | 2467.4 | 0 | 75.8 | 0 |  | 28.0463 | 2423.2
3 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.95 | 9080 | 41.61 | 3346.2 | -240 | 2234.5 | 2474.5 | 10.1 | 84.5953 | 2072 | 0 | 162.5 | 0 |  | 28.64 | 2474.5
4 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 40 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.9 | 8960 | 41.73 | 3486.6 | -120 | 2354.5 | 2474.5 | 10.1 | 84.6939 | 2189.5 | 0 | 165 | 0 |  | 28.64 | 2474.5
5 | 355 | 180 | 535 | 0 | 0 | 3 | 535 | 100 | 6.95 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.65 | 8360 | 41.64 | 3381.3 | -600 | 4803.5 | 5403.5 | 10.1 | 85.1903 | 4730.4 | 0 | 133.1 | 60 |  | 62.5405 | 5403.5
6 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 55 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.3 | 9920 | 41.9 | 3685.5 | 1560 | 5871.4043 | 3838 | 10.1 | 83.9115 | 5577.2 | 473.4043 | 294.2043 | 0 |  | 44.4213 | 3838
7 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 55 | 7.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.8 | 8720 | 41.61 | 3346.2 | -1200 | 2436 | 3636 | 10.1 | 84.8917 | 2264.8 | 0 | 171.2 | 0 |  | 42.0833 | 3636
8 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 40 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.15 | 9560 | 41.47 | 3182.4 | 840 | 5218.7632 | 2373.5 | 10.1 | 84.2032 | 5115 | 2005.2632 | 103.7632 | 0 |  | 27.4711 | 2373.5
9 | 285 | 0 | 285 | 0 | 0 | 3 | 285 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85 | 9200 | 41.72 | 3474.9 | -360 | 2518.5 | 2878.5 | 10.1 | 84.4969 | 2372.5 | 0 | 146 | 0 |  | 33.316 | 2878.5
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 40 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85 | 9200 | 41.32 | 3006.9 | 0 | 1749 | 1749 | 10.6 | 80.5112 | 1597.5 | 0 | 151.5 | 0 |  | 20.2431 | 1749
11 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200 | 40.9 | 2515.5 | 0 | 2015.0363 | 1414 | 10.1 | 84.4969 | 1849.75 | 601.0363 | 165.2863 | 0 |  | 16.3657 | 1414
12 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 55 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480 | 41.22 | 2889.9 | -720 | 1956.5 | 2676.5 | 10.1 | 85.0905 | 1788.5 | 0 | 168 | 0 |  | 30.978 | 2676.5
13 | 260 | 0 | 260 | 0 | 0 | 3 | 260 | 55 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480 | 41.69 | 3439.8 | 0 | 2626 | 2626 | 10.1 | 85.0905 | 2528.4 | 0 | 97.6 | 0 |  | 30.3935 | 2626
14 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 40 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.65 | 8360 | 41.53 | 3252.6 | -120 | 1568 | 1688 | 10.55 | 81.5566 | 1366.55 | 0 | 201.45 | 0 |  | 19.537 | 1688
15 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 55 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.6 | 8240 | 41.45 | 3159 | -120 | 1682.5 | 1802.5 | 10.3 | 83.6342 | 1570.4 | 0 | 142.1 | 30 |  | 20.8623 | 1802.5
16 | 0 | 180 | 180 | 0 | 0 | 4 | 180 | 54 | 0 | 3.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.7 | 8480 | 41.5 | 3217.5 | 240 | 2058 | 1818 | 10.1 | 85.0905 | 1778 | 0 | 280 | 0 |  | 21.0417 | 1818
17 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 54 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.15 | 9560 | 40.7 | 2281.5 | 1080 | 3868.883 | 682.5 | 10.5 | 80.9954 | 3620.8 | 2106.383 | 248.083 | 0 |  | 7.8993 | 682.5
18 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.15 | 9560 | 40.05 | 1521 | 0 | 858.5 | 858.5 | 10.1 | 84.2032 | 788.4 | 0 | 130.1 | 60 |  | 9.9363 | 858.5
19 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85.25 | 9800 | 39.57 | 959.4 | 240 | 1032 | 792 | 9.9 | 85.7056 | 836.2 | 0 | 195.8 | 0 |  | 9.1667 | 792
20 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 42 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.1 | 9440 | 39.74 | 1158.3 | -360 | 902.5 | 1262.5 | 10.1 | 84.3008 | 722.7 | 0 | 179.8 | 0 |  | 14.6123 | 1262.5
21 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 85.35 | 10040 | 40.73 | 2316.6 | 600 | 2728.5 | 2128.5 | 9.9 | 85.5079 | 2475 | 0 | 253.5 | 0 |  | 24.6354 | 2128.5
22 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.25 | 9800 | 41 | 2632.5 | -240 | 3647.8158 | 1161.5 | 10.1 | 84.0085 | 3555.1 | 2726.3158 | 92.7158 | 0 |  | 13.4433 | 1161.5
23 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 40 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.2 | 9680 | 41.42 | 3123.9 | -120 | 1193 | 1313 | 10.1 | 84.1057 | 1168 | 0 | 85 | 60 |  | 15.1968 | 1313
24 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.25 | 9800 | 41.32 | 3006.9 | 120 | 770 | 650 | 10 | 84.8486 | 737.2 | 0 | 32.8 | 0 |  | 7.5231 | 650
25 | 0 | 140 | 140 | 0 | 0 | 3 | 140 | 35 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.5 | 8000 | 41.9 | 3685.5 | -1800 | 2528.3404 | 1456 | 10.4 | 83.0249 | 2401.7 | 2872.3404 | 186.6404 | 60 |  | 16.8519 | 1456
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.6 | 8240 | 41.62 | 3357.9 | 240 | 961 | 721 | 10.3 | 83.6342 | 773.8 | 0 | 247.2 | 60 |  | 8.3449 | 721
27 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.7 | 8480 | 41.48 | 3194.1 | 240 | 982.5 | 742.5 | 9.9 | 86.8095 | 851.2 | 0 | 131.3 | 0 |  | 8.5938 | 742.5
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.6 | 8240 | 41.51 | 3229.2 | -240 | 2041.1915 | 728 | 10.4 | 82.83 | 1949.1 | 1553.1915 | 92.0915 | 0 |  | 8.4259 | 728
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.5 | 8000 | 41.58 | 3311.1 | -240 | 5283.9149 | 742 | 10.6 | 81.4584 | 5069.2 | 4781.9149 | 214.7149 | 0 |  | 8.588 | 742
30 | 0 | 150 | 150 | 0 | 0 | 3 | 150 | 54 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 83.2 | 4880 | 41.62 | 3357.9 | -3120 | 636.9355 | 1515 | 10.1 | 88.1885 | 674.5 | 2241.9355 | 22.4355 | 60 |  | 17.5347 | 1515
31 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 40 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 83.65 | 5960 | 41.69 | 3439.8 | 1080 | 2508.25 | 1428.25 | 9.85 | 89.4498 | 2316.95 | 0 | 191.3 | 0 |  | 16.5307 | 1428.25
| 2960 | 2763 | 5723 | 0 | 0 | 105 | 5618 | 100 | 70.1 | 64.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 |  |  | 84.8258 | 8781.9355 | 41.3152 | 3001.2387 | -3360 | 74084.7347 | 58082.95 | 10.149 | 84.4306 | 69593.55 | 19361.7847 | 4881.1847 | 390 |  | 21.6857 | 58082.95