## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 140 | 10 | 150 | 0 | 0 | 4 | 150 | 55 | 3.05 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85.1 | 9440 | 41.42 | 3123.9 | 3480 | 4995 | 1515 | 10.1 | 84.3008 | 4883.7 | 0 | 171.3 | 60 |  | 17.5347 | 1515
2 | 235 | 270 | 505 | 0 | 0 | 4 | 505 | 110 | 4.85 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 2 | 84 | 6800 | 41.62 | 3357.9 | -2640 | 2662.5 | 5302.5 | 10.5 | 83.2132 | 2635.3 | 0 | 87.2 | 60 |  | 61.3715 | 5302.5
3 | 115 | 90 | 205 | 0 | 0 | 3 | 205 | 110 | 2.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.3 | 7520 | 41.47 | 3182.4 | 720 | 2790.5 | 2070.5 | 10.1 | 85.8952 | 2499 | 0 | 291.5 | 0 |  | 23.9641 | 2070.5
4 | 35 | 40 | 75 | 0 | 0 | 4 | 75 | 35 | 0.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.35 | 7640 | 41.38 | 3077.1 | 120 | 907.5 | 787.5 | 10.5 | 82.5254 | 730 | 0 | 237.5 | 60 |  | 9.1146 | 787.5
5 | 85 | 20 | 105 | 0 | 0 | 3 | 105 | 80 | 2.6 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.1 | 7040 | 41.38 | 3077.1 | -600 | 4215.1968 | 1107.75 | 10.55 | 82.6221 | 4167.45 | 3707.4468 | 47.7468 | 0 |  | 12.8212 | 1107.75
6 | 0 | 40 | 40 | 0 | 0 | 4 | 40 | 35 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.25 | 5000 | 41.13 | 2784.6 | -2040 | 2953.1489 | 424 | 10.6 | 83.9268 | 2970 | 4569.1489 | 43.1489 | 60 |  | 4.9074 | 424
7 | 100 | 60 | 160 | 0 | 0 | 3 | 160 | 95 | 1.9 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 83.45 | 5480 | 41.85 | 3627 | 480 | 5553.617 | 1680 | 10.5 | 84.3173 | 5467.7 | 3393.617 | 145.917 | 60 |  | 19.4444 | 1680
8 | 90 | 260 | 350 | 0 | 0 | 4 | 350 | 103 | 1.8 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 8 | 84.65 | 8360 | 41.84 | 3615.3 | 2880 | 6415 | 3535 | 10.1 | 85.1903 | 6223 | 0 | 252 | 60 |  | 40.9144 | 3535
9 | 85 | 25 | 110 | 0 | 0 | 3 | 110 | 85 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.85 | 8840 | 41.47 | 3182.4 | 480 | 1569 | 1089 | 9.9 | 86.5057 | 1305 | 0 | 264 | 0 |  | 12.6042 | 1089
10 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84 | 6800 | 40.92 | 2538.9 | -2040 | 3818.6387 | 0 | 10.1 |  | 3792.4 | 5858.6387 | 86.2387 | 60 |  | 0 | 0
11 | 140 | 135 | 275 | 0 | 0 | 4 | 275 | 100 | 2.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.7 | 8480 | 41.56 | 3287.7 | 1680 | 8370.6915 | 2887.5 | 10.5 | 81.849 | 8371.65 | 3803.1915 | 59.0415 | 60 |  | 33.4201 | 2887.5
12 | 200 | 215 | 415 | 0 | 0 | 3 | 415 | 108 | 4.9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 12 | 84.55 | 8120 | 42.09 | 3907.8 | -360 | 4832.7105 | 4108.5 | 9.9 | 87.1156 | 4687.5 | 1084.2105 | 145.2105 | 0 |  | 47.5521 | 4108.5
13 | 110 | 75 | 185 | 0 | 0 | 4 | 185 | 95 | 2.1 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 83.05 | 4520 | 41.26 | 2936.7 | -3600 | 3097.5851 | 1979.5 | 10.7 | 83.5475 | 3143 | 4718.0851 | 104.5851 | 150 |  | 22.9109 | 1979.5
14 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 83.5 | 5600 | 40.73 | 2316.6 | 1080 | 1080 | 0 | 10.1 |  | 767.6 | 0 | 312.4 | 0 |  | 0 | 0
15 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 83.5 | 5600 | 40.93 | 2550.6 | 0 | 795 | 795 | 10.6 | 83.4212 | 675 | 0 | 120 | 0 |  | 9.2014 | 795
16 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.5 | 5600 | 41.09 | 2737.8 | 0 | 721 | 721 | 10.3 | 85.851 | 693.5 | 0 | 92.5 | 65 |  | 8.3449 | 721
17 | 105 | 85 | 190 | 0 | 0 | 4 | 190 | 110 | 2 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 82.85 | 4070 | 42.02 | 3825.9 | -1530 | 611.6383 | 1881 | 9.9 | 90.7409 | 617.7 | 260.6383 | 93.9383 | 100 |  | 21.7708 | 1881
18 | 35 | 35 | 70 | 0 | 0 | 3 | 70 | 70 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 82.85 | 4070 | 42.14 | 3966.3 | 0 | 707 | 707 | 10.1 | 88.9441 | 693.5 | 0 | 73.5 | 60 |  | 8.1829 | 707
19 | 30 | 30 | 60 | 0 | 0 | 3 | 60 | 70 | 0.85 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 83.15 | 4760 | 41.94 | 3732.3 | 690 | 3046 | 606 | 10.1 | 88.2957 | 2941.9 | 1750 | 134.1 | 30 |  | 7.0139 | 606
20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 83.4 | 5360 | 41.45 | 3159 | 600 | 4084.0426 | 0 | 10.1 |  | 3927.4 | 3484.0426 | 186.6426 | 30 |  | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 83.3 | 5120 | 41 | 2632.5 | -240 | 807.8723 | 0 | 10.1 |  | 630 | 1047.8723 | 177.8723 | 0 |  | 0 | 0
22 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.2 | 4880 | 41.22 | 2889.9 | -240 | 1309.8947 | 792 | 9.9 | 89.9701 | 1072.5 | 757.8947 | 237.3947 | 0 |  | 9.1667 | 792
23 | 154 | 79 | 233 | 0 | 0 | 4 | 233 | 108 | 3.75 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.35 | 10040 | 41.81 | 3580.2 | 5160 | 7807.7083 | 2330 | 10 | 84.6528 | 7717.5 | 317.7083 | 90.2083 | 0 |  | 26.9676 | 2330
24 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.7 | 8480 | 41.16 | 2819.7 | -1560 | 237.8723 | 0 | 10.1 |  | 0 | 1797.8723 | 237.8723 | 0 |  | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 84.7 | 8480 | 40.66 | 2234.7 | 0 | 0 | 0 | 10.1 |  | 0 | 0 | 60 | 60 |  | 0 | 0
26 | 0 | 71 | 71 | 0 | 0 | 3 | 71 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600 | 40.79 | 2386.8 | 120 | 822.9 | 702.9 | 9.9 | 86.708 | 712.5 | 0 | 110.4 | 0 |  | 8.1354 | 702.9
27 | 71 | 0 | 71 | 0 | 0 | 4 | 71 | 35 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.75 | 8600 | 40.88 | 2492.1 | 0 | 745.5 | 745.5 | 10.5 | 81.7533 | 675 | 0 | 70.5 | 0 |  | 8.6285 | 745.5
28 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.1 | 9440 | 41.01 | 2644.2 | 840 | 3298.0769 | 735 | 10.5 | 81.0894 | 3207.2 | 1723.0769 | 90.8769 | 0 |  | 8.5069 | 735
29 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280 | 41.14 | 2796.3 | -2160 | 1313.6684 | 848 | 10.6 | 82.0375 | 1365.1 | 2625.6684 | 48.5684 | 100 |  | 9.8148 | 848
30 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 47 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.1 | 7040 | 41.33 | 3018.6 | -240 | 3000.515 | 912.39 | 10.734 | 81.2058 | 2835 | 2328.125 | 165.515 | 0 |  | 10.5601 | 912.39
| 1885 | 1845 | 3730 | 0 | 0 | 104 | 3626 | 110 | 41.9 | 42.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 |  |  | 84.0417 | 6902 | 41.3563 | 3049.41 | 1080 | 82569.7776 | 38262.54 | 10.2581 | 85.0914 | 79407.1 | 43227.2376 | 4237.6776 | 1075 |  | 14.7618 | 38262.54