## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 55 | 5.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 3 | 0 | ΒΛΑΒΗ ΟΡΙΟΥ ΦΟΡΤΙΟΥ | 1 | 85.2 | 9680 | 41.83 | 3603.6 | 2640 | 8130.6383 | 1980 | 9.9 | 85.8048 | 7862.1 | 3510.6383 | 268.5383 | 0 |  | 22.9167 | 1980
2 | 85 | 90 | 175 | 0 | 0 | 4 | 175 | 55 | 1.7 | 1.7 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΧΑΜΗΛΗ ΣΤΑΘΜΗ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡ | 2 | 85.3 | 9920 | 42.03 | 3837.6 | 240 | 5483.1383 | 1732.5 | 9.9 | 85.6066 | 5511.5 | 3510.6383 | 71.6383 | 100 |  | 20.0521 | 1732.5
3 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 55 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.55 | 8120 | 41.34 | 3030.3 | -1800 | 1785.4167 | 1575 | 10.5 | 82.1375 | 1547.6 | 2010.4167 | 237.8167 | 0 |  | 18.2292 | 1575
4 | 105 | 140 | 245 | 0 | 0 | 4 | 245 | 110 | 2.2 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 85.35 | 10040 | 41.72 | 3474.9 | 1920 | 4909.6026 | 2425.5 | 9.9 | 85.5079 | 4672.5 | 564.1026 | 237.1026 | 0 |  | 28.0729 | 2425.5
5 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.8 | 8720 | 41.43 | 3135.6 | -1320 | 2896.7949 | 945 | 10.5 | 81.6578 | 2902.5 | 3271.7949 | 94.2949 | 100 |  | 10.9375 | 945
6 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.35 | 7640 | 41.7 | 3451.5 | -1080 | 3268.4585 | 892.5 | 10.5 | 82.5254 | 3212 | 3455.9585 | 116.4585 | 60 |  | 10.3299 | 892.5
7 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 83.25 | 5000 | 41.23 | 2901.6 | -2640 | 1616.2766 | 735 | 10.5 | 84.7261 | 1620.6 | 3521.2766 | 95.6766 | 100 |  | 8.5069 | 735
8 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.6 | 5840 | 41.19 | 2854.8 | 840 | 3196.7462 | 707 | 10.1 | 87.3405 | 3123.75 | 1649.7462 | 72.9962 | 0 |  | 8.1829 | 707
9 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.2 | 7280 | 41.28 | 2960.1 | 1440 | 3886.7959 | 707 | 10.1 | 86.0987 | 3737.6 | 1739.7959 | 149.1959 | 0 |  | 8.1829 | 707
10 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.65 | 5960 | 41.46 | 3170.7 | -1320 | 3091.7351 | 943.65 | 10.485 | 84.0325 | 3146.3 | 3468.0851 | 25.4351 | 80 |  | 10.9219 | 943.65
11 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 55 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.5 | 5600 | 41.52 | 3240.9 | -360 | 2905.6224 | 959.5 | 10.1 | 87.551 | 2868.9 | 2306.1224 | 76.7224 | 40 |  | 11.1053 | 959.5
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 83.35 | 5240 | 41.5 | 3217.5 | -360 | 2616.8878 | 757.5 | 10.1 | 87.8686 | 2555 | 2219.3878 | 61.8878 | 0 |  | 8.7674 | 757.5
13 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 45 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 82.95 | 4290 | 41.52 | 3240.9 | -950 | 3089.6429 | 682.5 | 10.5 | 85.3468 | 3124.4 | 3357.1429 | 25.2429 | 60 |  | 7.8993 | 682.5
14 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 82.5 | 3300 | 41.56 | 3287.7 | -990 | 1638.7713 | 1011.75 | 10.65 | 85.0797 | 1587.75 | 1617.0213 | 111.0213 | 60 |  | 11.7101 | 1011.75
15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 83.9 | 6560 | 41.09 | 2737.8 | 3260 | 5531.3568 | 0 | 10.1 |  | 5350.8 | 2271.3568 | 180.5568 | 0 |  | 0 | 0
16 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.8 | 6320 | 41.24 | 2913.3 | -240 | 3851.383 | 735 | 10.5 | 83.6113 | 3832.5 | 3356.383 | 78.883 | 60 |  | 8.5069 | 735
17 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.9 | 6560 | 41.53 | 3252.6 | 240 | 4541.383 | 945 | 10.5 | 83.4118 | 4526 | 3356.383 | 75.383 | 60 |  | 10.9375 | 945
18 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.8 | 6320 | 41.34 | 3030.3 | -240 | 4594.7368 | 840 | 10.5 | 83.6113 | 4627.5 | 3994.7368 | 67.2368 | 100 |  | 9.7222 | 840
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.65 | 5960 | 41.4 | 3100.5 | -360 | 4369.6809 | 735 | 10.5 | 83.9124 | 4350.8 | 3994.6809 | 78.8809 | 60 |  | 8.5069 | 735
20 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 83.1 | 4640 | 41.5 | 3217.5 | -1320 | 3787.8947 | 1050 | 10.5 | 85.0353 | 3781.4 | 4057.8947 | 66.4947 | 60 |  | 12.1528 | 1050
21 | 45 | 0 | 45 | 0 | 0 | 3 | 45 | 35 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 82.85 | 4070 | 41.31 | 2995.2 | -570 | 3961.7431 | 462.96 | 10.288 | 87.3188 | 3934.7 | 4068.7831 | 87.0431 | 60 |  | 5.3583 | 462.96
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 50 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.4 | 5360 | 41.48 | 3194.1 | 1290 | 2148.5 | 858.5 | 10.1 | 87.7625 | 1980 | 0 | 168.5 | 0 |  | 9.9363 | 858.5
23 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.95 | 6680 | 41.46 | 3170.7 | 1320 | 2027 | 707 | 10.1 | 86.6118 | 1970.55 | 0 | 56.45 | 0 |  | 8.1829 | 707
24 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.95 | 6680 | 41.51 | 3229.2 | 0 | 707 | 707 | 10.1 | 86.6118 | 641.75 | 0 | 65.25 | 0 |  | 8.1829 | 707
25 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84 | 6800 | 41.5 | 3217.5 | 120 | 827 | 707 | 10.1 | 86.5087 | 671.95 | 0 | 155.05 | 0 |  | 8.1829 | 707
26 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.45 | 5480 | 41.56 | 3287.7 | -1320 | 3605.8575 | 858.5 | 10.1 | 87.6566 | 3555.1 | 4067.3575 | 50.7575 | 0 |  | 9.9363 | 858.5
27 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.25 | 5000 | 41.55 | 3276 | -480 | 2369.3782 | 1010 | 10.1 | 88.0816 | 2256.45 | 1839.3782 | 112.9282 | 0 |  | 11.6898 | 1010
28 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 83 | 4400 | 41.47 | 3182.4 | -600 | 3691.25 | 791.25 | 10.55 | 84.8387 | 3686.4 | 3500 | 64.85 | 60 |  | 9.158 | 791.25
29 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83 | 4400 | 41.06 | 2702.7 | 0 | 4479.7222 | 757.5 | 10.1 | 88.6187 | 4403 | 3722.2222 | 76.7222 | 0 |  | 8.7674 | 757.5
30 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 83.15 | 4760 | 40.9 | 2515.5 | 360 | 4328.7801 | 707 | 10.1 | 88.2957 | 4365.4 | 3261.7801 | 23.3801 | 60 |  | 8.1829 | 707
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 82.95 | 4290 | 40.91 | 2527.2 | -470 | 4332.7447 | 707 | 10.1 | 88.7269 | 4282.85 | 4095.7447 | 109.8947 | 60 |  | 8.1829 | 707
| 1710 | 1090 | 2800 | 0 | 0 | 103 | 2697 | 110 | 41.3 | 26.8 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0.78 | 0 | 23 | 13 |  |  | 83.7306 | 6158.3871 | 41.4232 | 3127.6742 | -2750 | 107671.9384 | 28633.11 | 10.2261 | 85.9934 | 105689.65 | 81788.8284 | 3162.2884 | 1180 |  | 10.6904 | 28633.11