## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.2 | 4880 | 40.93 | 2550.6 | 590 | 4482.567 | 707 | 10.1 | 88.1885 | 4496.8 | 3185.567 | 45.767 | 60 |  | 8.1829 | 707
2 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.25 | 5000 | 40.9 | 2515.5 | 120 | 4452 | 707 | 10.1 | 88.0816 | 4462.55 | 3625 | 49.45 | 60 |  | 8.1829 | 707
3 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.15 | 4760 | 40.9 | 2515.5 | -240 | 4558.4921 | 735 | 10.5 | 84.932 | 4572 | 4063.4921 | 46.4921 | 60 |  | 8.5069 | 735
4 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.5 | 5600 | 41.16 | 2819.7 | 840 | 5979.4737 | 1050 | 10.5 | 84.2157 | 5860.8 | 4089.4737 | 178.6737 | 60 |  | 12.1528 | 1050
5 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.5 | 5600 | 41.17 | 2831.4 | 0 | 735 | 735 | 10.5 | 84.2157 | 627.8 | 0 | 167.2 | 60 |  | 8.5069 | 735
6 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.55 | 5720 | 41.26 | 2936.7 | 120 | 827 | 707 | 10.1 | 87.4456 | 657 | 0 | 170 | 0 |  | 8.1829 | 707
7 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 55 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.45 | 7880 | 41.3 | 2983.5 | 2160 | 3290.6122 | 850 | 10 | 86.4476 | 3042.65 | 280.6122 | 247.9622 | 0 |  | 9.838 | 850
8 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.9 | 6560 | 41.32 | 3006.9 | -1320 | 2925.6383 | 735 | 10.5 | 83.4118 | 2867.15 | 3510.6383 | 118.4883 | 60 |  | 8.5069 | 735
9 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 83.6 | 5840 | 41.33 | 3018.6 | -720 | 3350.0851 | 852 | 10.65 | 82.83 | 3248.5 | 3218.0851 | 161.5851 | 60 |  | 9.8611 | 852
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.6 | 5840 | 41.23 | 2901.6 | 0 | 1267.2094 | 707 | 10.1 | 87.3405 | 1073 | 560.2094 | 194.2094 | 0 |  | 8.1829 | 707
11 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.5 | 5600 | 41.38 | 3077.1 | -240 | 3642.5319 | 707 | 10.1 | 87.551 | 3547.8 | 3175.5319 | 154.7319 | 60 |  | 8.1829 | 707
12 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 83.55 | 5720 | 41.5 | 3217.5 | 120 | 3757.4362 | 738.5 | 10.55 | 83.7157 | 3372.6 | 2898.9362 | 444.8362 | 60 |  | 8.5475 | 738.5
13 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 83.5 | 5600 | 41.5 | 3217.5 | -120 | 4538.4574 | 892.5 | 10.5 | 84.2157 | 4387.3 | 3765.9574 | 211.1574 | 60 |  | 10.3299 | 892.5
14 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.9 | 8960 | 41.57 | 3299.4 | 3360 | 6456.7021 | 735 | 10.5 | 81.4674 | 6394.8 | 2361.7021 | 121.9021 | 60 |  | 8.5069 | 735
15 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.75 | 8600 | 41.56 | 3287.7 | -360 | 2102.3191 | 707 | 10.1 | 84.991 | 1992.9 | 1755.3191 | 169.4191 | 60 |  | 8.1829 | 707
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.9 | 8960 | 41.54 | 3264.3 | 360 | 1067 | 707 | 10.1 | 84.6939 | 1014.7 | 0 | 52.3 | 0 |  | 8.1829 | 707
17 | 165 | 70 | 235 | 0 | 0 | 3 | 235 | 85 | 3.5 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.35 | 10040 | 41.64 | 3381.3 | 1080 | 3406.5 | 2326.5 | 9.9 | 85.5079 | 3210.9 | 0 | 195.6 | 0 |  | 26.9271 | 2326.5
18 | 45 | 100 | 145 | 0 | 0 | 4 | 145 | 45 | 1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 2 | 2 | ΒΛΑΒΗ ΑΝΤΛΙΑΣ ΜΙΤΣΕΛ | 18 | 84.55 | 8120 | 40.93 | 2550.6 | -1920 | 890.8311 | 1529.75 | 10.55 | 81.7483 | 812 | 1281.0811 | 228.8311 | 150 |  | 17.7054 | 1529.75
19 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.6 | 8240 | 40.55 | 2106 | 120 | 877.5 | 757.5 | 10.1 | 85.2903 | 676.2 | 0 | 201.3 | 0 |  | 8.7674 | 757.5
20 | 90 | 460 | 550 | 0 | 0 | 3 | 550 | 100 | 2.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 85.3 | 9920 | 41.75 | 3510 | 1680 | 7345 | 5665 | 10.3 | 82.2821 | 7282.5 | 0 | 62.5 | 0 |  | 65.5671 | 5665
21 | 190 | 105 | 295 | 0 | 0 | 2 | 295 | 45 | 4.5 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 21 | 84.7 | 8480 | 41.72 | 3474.9 | -1440 | 1598.5 | 3038.5 | 10.3 | 83.4383 | 1530 | 0 | 68.5 | 0 |  | 35.1678 | 3038.5
22 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.8 | 8720 | 41.22 | 2889.9 | 240 | 947 | 707 | 10.1 | 84.8917 | 678.9 | 0 | 328.1 | 60 |  | 8.1829 | 707
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 43 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.8 | 8720 | 40.9 | 2515.5 | 0 | 800 | 800 | 10 | 85.7407 | 715.2 | 0 | 84.8 | 0 |  | 9.2593 | 800
24 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.9 | 8960 | 40.67 | 2246.4 | 240 | 940 | 700 | 10 | 85.5408 | 762.2 | 0 | 177.8 | 0 |  | 8.1019 | 700
25 | 130 | 150 | 280 | 0 | 0 | 3 | 280 | 70 | 3.6 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.1 | 7040 | 41.31 | 2995.2 | -1920 | 880 | 2800 | 10 | 87.1663 | 737.3 | 0 | 142.7 | 0 |  | 32.4074 | 2800
26 | 300 | 470 | 770 | 0 | 0 | 3 | 770 | 109 | 5.7 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.9 | 8960 | 41.72 | 3474.9 | 1920 | 9912.5532 | 7700 | 10 | 85.5408 | 9752.6 | 292.5532 | 159.9532 | 0 |  | 89.1204 | 7700
27 | 460 | 370 | 830 | 0 | 0 | 4 | 830 | 110 | 10 | 7.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 85.1 | 9440 | 41.85 | 3627 | 480 | 9112 | 8632 | 10.4 | 81.8691 | 9075 | 0 | 37 | 0 |  | 99.9074 | 8632
28 | 160 | 610 | 770 | 0 | 0 | 4 | 770 | 110 | 3.5 | 15.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.4 | 7760 | 41.67 | 3416.4 | -1680 | 6097 | 7777 | 10.1 | 85.6926 | 5905.7 | 0 | 191.3 | 0 |  | 90.0116 | 7777
29 | 570 | 20 | 590 | 0 | 0 | 3 | 590 | 110 | 14 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.5 | 8000 | 41.74 | 3498.3 | 240 | 6199 | 5959 | 10.1 | 85.491 | 6141.6 | 0 | 57.4 | 0 |  | 68.9699 | 5959
30 | 45 | 390 | 435 | 0 | 0 | 4 | 435 | 110 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.4 | 7760 | 41.98 | 3779.1 | -240 | 4153.5 | 4393.5 | 10.1 | 85.6926 | 3974.4 | 0 | 179.1 | 0 |  | 50.8507 | 4393.5
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.4 | 7760 | 41.24 | 2913.3 | 0 | 1866.5745 | 707 | 10.1 | 85.6926 | 1689.8 | 1159.5745 | 176.7745 | 0 |  | 8.1829 | 707
| 3120 | 3335 | 6455 | 0 | 0 | 102 | 6353 | 110 | 76.1 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 31 | 21 |  |  | 84.2452 | 7388.3871 | 41.3368 | 3026.5258 | 3470 | 108458.4834 | 65764.75 | 10.1882 | 85.2622 | 104562.65 | 39223.7334 | 4825.8334 | 930 |  | 24.5537 | 65764.75