## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 54 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.9 | 8960 | 41.15 | 2808 | 1200 | 3624 | 2424 | 10.1 | 84.6939 | 3460.2 | 0 | 163.8 | 0 |  | 28.0556 | 2424
2 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.35 | 10040 | 41.18 | 2843.1 | 1080 | 1787 | 707 | 10.1 | 83.8147 | 1642.8 | 0 | 144.2 | 0 |  | 8.1829 | 707
3 | 105 | 340 | 445 | 0 | 0 | 4 | 445 | 108 | 2.6 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 85.45 | 10320 | 41.44 | 3147.3 | 280 | 4774.5 | 4494.5 | 10.1 | 83.6218 | 4717.5 | 0 | 57 | 0 |  | 52.0197 | 4494.5
4 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 55 | 0 | 14.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.1 | 9440 | 41.64 | 3381.3 | -880 | 5220 | 6100 | 10 | 85.1439 | 5067.75 | 0 | 152.25 | 0 |  | 70.6019 | 6100
5 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 45 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200 | 40.74 | 2328.3 | -240 | 600 | 840 | 10.5 | 81.278 | 572.7 | 0 | 87.3 | 60 |  | 9.7222 | 840
6 | 35 | 270 | 305 | 0 | 0 | 3 | 305 | 80 | 0.95 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 |  | 6 | 84.2 | 7280 | 40.96 | 2585.7 | -1920 | 1160.5 | 3080.5 | 10.1 | 86.0987 | 904.05 | 0 | 256.45 | 0 |  | 35.6539 | 3080.5
7 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.2 | 7280 | 41.08 | 2726.1 | 0 | 4570.1579 | 707 | 10.1 | 86.0987 | 4555.2 | 3863.1579 | 74.9579 | 60 |  | 8.1829 | 707
8 | 25 | 155 | 180 | 0 | 0 | 4 | 180 | 45 | 0.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 83.95 | 6680 | 41.32 | 3006.9 | -600 | 1774.359 | 1800 | 10 | 87.4779 | 1646.4 | 574.359 | 127.959 | 0 |  | 20.8333 | 1800
9 | 155 | 130 | 285 | 0 | 0 | 3 | 285 | 70 | 4.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.75 | 6200 | 41.63 | 3369.6 | -480 | 4137.8617 | 2878.5 | 10.1 | 87.0267 | 4161 | 1739.3617 | 36.8617 | 60 |  | 33.316 | 2878.5
10 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.9 | 8960 | 41.3 | 2983.5 | 2760 | 7251.5426 | 2257.5 | 10.5 | 81.4674 | 7161.3 | 2234.0426 | 150.2426 | 60 |  | 26.1285 | 2257.5
11 | 375 | 345 | 720 | 0 | 0 | 4 | 720 | 110 | 8.4 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 |  | 11 | 85 | 9200 | 41.77 | 3533.4 | 240 | 11050 | 7560 | 10.5 | 81.278 | 11059.5 | 3250 | 90.5 | 100 |  | 87.5 | 7560
12 | 0 | 405 | 405 | 0 | 0 | 3 | 405 | 55 | 0 | 9.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.1 | 9440 | 41.23 | 2901.6 | 240 | 6625.8368 | 4090.5 | 10.1 | 84.3008 | 6556.2 | 2295.3368 | 69.6368 | 0 |  | 47.3438 | 4090.5
13 | 705 | 80 | 785 | 0 | 0 | 4 | 785 | 110 | 13.1 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.1 | 9440 | 41.8 | 3568.5 | 0 | 8886.6492 | 7850 | 10 | 85.1439 | 8627.1 | 1036.6492 | 259.5492 | 0 |  | 90.8565 | 7850
14 | 715 | 0 | 715 | 0 | 0 | 4 | 715 | 55 | 13.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 1 | 0 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 14 | 83.7 | 6080 | 41.67 | 3416.4 | -3360 | 6965.967 | 7293 | 10.2 | 86.2769 | 6881 | 3032.967 | 144.967 | 60 |  | 84.4097 | 7293
15 | 650 | 0 | 650 | 0 | 0 | 3 | 650 | 55 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 15 | 83.55 | 5720 | 41.59 | 3322.8 | -360 | 9340.4645 | 6695 | 10.3 | 85.7477 | 9338 | 3005.4645 | 62.4645 | 60 |  | 77.4884 | 6695
16 | 225 | 415 | 640 | 0 | 0 | 4 | 640 | 55 | 4.5 | 12.25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 | 1 | 2 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 16 | 84.1 | 7040 | 41.75 | 3510 | 1320 | 9848.5161 | 6464 | 10.1 | 86.3032 | 9828 | 2064.5161 | 80.5161 | 60 |  | 74.8148 | 6464
17 | 850 | 0 | 850 | 0 | 0 | 3 | 850 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.75 | 6200 | 41.69 | 3439.8 | -840 | 10813.0405 | 8712.5 | 10.25 | 85.7532 | 10885 | 2940.5405 | 28.0405 | 100 |  | 100.8391 | 8712.5
18 | 785 | 305 | 1090 | 0 | 0 | 4 | 1090 | 85 | 16.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.4 | 7760 | 41.64 | 3381.3 | 1560 | 17079.4681 | 11445 | 10.5 | 82.4281 | 17056.8 | 4074.4681 | 82.6681 | 60 |  | 132.4653 | 11445
19 | 705 | 0 | 705 | 0 | 0 | 3 | 705 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.9 | 8960 | 41.68 | 3428.1 | 1200 | 8320.5 | 7120.5 | 10.1 | 84.6939 | 7999.4 | 0 | 321.1 | 0 |  | 82.4132 | 7120.5
20 | 245 | 450 | 695 | 0 | 0 | 4 | 695 | 90 | 5.25 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 1 | 1 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 20 | 84.85 | 8840 | 41.63 | 3369.6 | -120 | 6899.5 | 7019.5 | 10.1 | 84.7927 | 6762 | 0 | 137.5 | 0 |  | 81.2442 | 7019.5
21 | 255 | 275 | 530 | 0 | 0 | 4 | 530 | 55 | 4.65 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.9 | 6560 | 41.6 | 3334.5 | -2280 | 5290.0955 | 5479.67 | 10.339 | 84.7106 | 5219.5 | 2090.4255 | 70.5955 | 0 |  | 63.4221 | 5479.67
22 | 265 | 360 | 625 | 0 | 0 | 4 | 625 | 90 | 5.05 | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 84.05 | 6920 | 41.61 | 3346.2 | 360 | 6672.5 | 6312.5 | 10.1 | 86.4059 | 6608.2 | 0 | 64.3 | 0 |  | 73.0613 | 6312.5
23 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 55 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 83.7 | 6080 | 41.05 | 2691 | -840 | 2919.5 | 3759.5 | 10.3 | 85.4392 | 2954 | 0 | 25.5 | 60 |  | 43.5127 | 3759.5
24 | 20 | 385 | 405 | 0 | 0 | 3 | 405 | 55 | 0.55 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84 | 6800 | 41.34 | 3030.3 | 720 | 5584.2021 | 4252.5 | 10.5 | 83.2132 | 5481.2 | 611.7021 | 103.0021 | 0 |  | 49.2188 | 4252.5
25 | 515 | 160 | 675 | 0 | 0 | 4 | 675 | 80 | 12 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.95 | 6680 | 41.1 | 2749.5 | -120 | 6963.4574 | 6817.5 | 10.1 | 86.6118 | 6902 | 265.9574 | 91.4574 | 30 |  | 78.9062 | 6817.5
26 | 35 | 220 | 255 | 0 | 0 | 3 | 255 | 50 | 0.9 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.35 | 7640 | 41.05 | 2691 | 960 | 3535.5 | 2575.5 | 10.1 | 85.7938 | 3571.92 | 0 | 23.58 | 60 |  | 29.809 | 2575.5
27 | 245 | 45 | 290 | 0 | 0 | 2 | 290 | 65 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 83.45 | 5480 | 41.05 | 2691 | -2160 | 1955.1702 | 2929 | 10.1 | 87.6566 | 1958.4 | 1186.1702 | 56.7702 | 60 |  | 33.9005 | 2929
28 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.05 | 4520 | 41.18 | 2843.1 | -960 | 3298.8511 | 2828 | 10.1 | 88.5108 | 3297.6 | 1430.8511 | 61.2511 | 60 |  | 32.7315 | 2828
| 7515 | 5665 | 13180 | 0 | 0 | 95 | 13085 | 110 | 154.2 | 128.7 | 0 | 0 | 0 | 0 | 0 | 0 | 55.3 | 0 | 31 | 28 |  |  | 84.3464 | 7632.8571 | 41.3882 | 3086.7107 | -3240 | 166949.1398 | 134493.17 | 10.2043 | 84.9237 | 164874.72 | 35695.9698 | 3024.4198 | 950 |  | 55.5941 | 134493.17