## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 280 | 135 | 415 | 0 | 0 | 3 | 415 | 55 | 6.6 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 1 | 84 | 6800 | 41.75 | 3510 | 2280 | 6554.5 | 4274.5 | 10.3 | 84.8289 | 6555.2 | 0 | 59.3 | 60 |  | 49.4734 | 4274.5
2 | 325 | 405 | 730 | 0 | 0 | 3 | 730 | 95 | 7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 2 | 85.15 | 9560 | 41.71 | 3463.2 | 2760 | 10133 | 7373 | 10.1 | 84.2032 | 10020.11 | 0 | 112.89 | 0 |  | 85.3356 | 7373
3 | 300 | 0 | 300 | 0 | 0 | 2 | 300 | 55 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.85 | 8840 | 41.22 | 2889.9 | -720 | 2873.8298 | 3030 | 10.1 | 84.7927 | 2744.8 | 563.8298 | 189.0298 | 60 |  | 35.0694 | 3030
4 | 0 | 255 | 255 | 0 | 0 | 3 | 255 | 55 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.6 | 8240 | 41.24 | 2913.3 | -600 | 1975.5 | 2575.5 | 10.1 | 85.2903 | 1890.7 | 0 | 144.8 | 60 |  | 29.809 | 2575.5
5 | 175 | 70 | 245 | 0 | 0 | 3 | 245 | 70 | 4.05 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84.65 | 8360 | 41.46 | 3170.7 | 120 | 2631.25 | 2511.25 | 10.25 | 83.9436 | 2595 | 0 | 36.25 | 0 |  | 29.0654 | 2511.25
6 | 85 | 260 | 345 | 0 | 0 | 3 | 345 | 85 | 1.85 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 6 | 84.1 | 7040 | 41.19 | 2854.8 | -1320 | 2164.5 | 3484.5 | 10.1 | 86.3032 | 2114 | 0 | 110.5 | 60 |  | 40.3299 | 3484.5
7 | 300 | 225 | 525 | 0 | 0 | 2 | 525 | 55 | 6.6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.55 | 8120 | 41.6 | 3334.5 | 1080 | 6382.5 | 5302.5 | 10.1 | 85.3905 | 6029.8 | 0 | 352.7 | 0 |  | 61.3715 | 5302.5
8 | 0 | 180 | 180 | 0 | 0 | 3 | 180 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.6 | 8240 | 41.2 | 2866.5 | 120 | 1938 | 1818 | 10.1 | 85.2903 | 1888.6 | 0 | 109.4 | 60 |  | 21.0417 | 1818
9 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 55 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.45 | 7880 | 41.5 | 3217.5 | -360 | 1963 | 2323 | 10.1 | 85.5917 | 1905.3 | 0 | 117.7 | 60 |  | 26.8866 | 2323
10 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.5 | 8000 | 41.2 | 2866.5 | 120 | 1988.5 | 1868.5 | 10.1 | 85.491 | 1890.7 | 0 | 157.8 | 60 |  | 21.6262 | 1868.5
11 | 235 | 0 | 235 | 0 | 0 | 2 | 235 | 55 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7640 | 41.01 | 2644.2 | -360 | 2013.5 | 2373.5 | 10.1 | 85.7938 | 1898 | 0 | 175.5 | 60 |  | 27.4711 | 2373.5
12 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 55 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800 | 41.05 | 2691 | -840 | 1902.75 | 2742.75 | 10.35 | 84.4191 | 1905.3 | 0 | 57.45 | 60 |  | 31.7448 | 2742.75
13 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 55 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.2 | 7280 | 41.12 | 2772.9 | 480 | 1995 | 1515 | 10.1 | 86.0987 | 1949.1 | 0 | 105.9 | 60 |  | 17.5347 | 1515
14 | 40 | 200 | 240 | 0 | 0 | 2 | 240 | 70 | 0.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.7 | 8480 | 41.1 | 2749.5 | 1200 | 3624 | 2424 | 10.1 | 85.0905 | 3529.8 | 0 | 94.2 | 0 |  | 28.0556 | 2424
15 | 150 | 130 | 280 | 0 | 0 | 3 | 280 | 110 | 3.1 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.1 | 7040 | 41.32 | 3006.9 | -1440 | 1388 | 2828 | 10.1 | 86.3032 | 1408.9 | 0 | 39.1 | 60 |  | 32.7315 | 2828
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.15 | 7160 | 41.42 | 3123.9 | 120 | 813 | 693 | 9.9 | 87.9423 | 675 | 0 | 138 | 0 |  | 8.0208 | 693
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.15 | 7160 | 41.42 | 3123.9 | 0 | 757.5 | 757.5 | 10.1 | 86.2009 | 682.5 | 0 | 75 | 0 |  | 8.7674 | 757.5
18 | 0 | 75 | 75 | 0 | 0 | 2 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.2 | 7280 | 41.45 | 3159 | 120 | 877.5 | 757.5 | 10.1 | 86.0987 | 683.55 | 0 | 193.95 | 0 |  | 8.7674 | 757.5
19 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.2 | 7280 | 41.48 | 3194.1 | 0 | 707 | 707 | 10.1 | 86.0987 | 664.3 | 0 | 42.7 | 0 |  | 8.1829 | 707
20 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.2 | 7280 | 41.23 | 2901.6 | 0 | 707 | 707 | 10.1 | 86.0987 | 668.85 | 0 | 38.15 | 0 |  | 8.1829 | 707
21 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.25 | 7400 | 41.33 | 3018.6 | 120 | 820 | 700 | 10 | 86.8568 | 703 | 0 | 117 | 0 |  | 8.1019 | 700
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.25 | 7400 | 41.56 | 3287.7 | 0 | 858.5 | 858.5 | 10.1 | 85.9968 | 680.8 | 0 | 177.7 | 0 |  | 9.9363 | 858.5
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 45 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.2 | 7280 | 41.55 | 3276 | -120 | 738.5 | 858.5 | 10.1 | 86.0987 | 658.6 | 0 | 79.9 | 0 |  | 9.9363 | 858.5
24 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.2 | 7280 | 41.43 | 3135.6 | 0 | 757.5 | 757.5 | 10.1 | 86.0987 | 649.7 | 0 | 107.8 | 0 |  | 8.7674 | 757.5
25 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 35 | 2.5 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280 | 41.65 | 3393 | 0 | 900 | 900 | 10 | 86.9597 | 694.6 | 0 | 205.4 | 0 |  | 10.4167 | 900
26 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.2 | 7280 | 41.47 | 3182.4 | 0 | 757.5 | 757.5 | 10.1 | 86.0987 | 660 | 0 | 97.5 | 0 |  | 8.7674 | 757.5
27 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.3 | 7520 | 41.45 | 3159 | 240 | 990 | 750 | 10 | 86.7541 | 727.5 | 0 | 262.5 | 0 |  | 8.6806 | 750
28 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.3 | 7520 | 41.63 | 3369.6 | 0 | 757.5 | 757.5 | 10.1 | 85.8952 | 697.5 | 0 | 60 | 0 |  | 8.7674 | 757.5
29 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.3 | 7520 | 41.63 | 3369.6 | 0 | 909 | 909 | 10.1 | 85.8952 | 685.4 | 0 | 223.6 | 0 |  | 10.5208 | 909
30 | 0 | 70 | 70 | 0 | 0 | 2 | 70 | 35 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.35 | 7640 | 41.58 | 3311.1 | 120 | 813 | 693 | 9.9 | 87.527 | 660 | 0 | 153 | 0 |  | 8.0208 | 693
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.35 | 7640 | 41.42 | 3123.9 | 0 | 750 | 750 | 10 | 86.6517 | 642.4 | 0 | 107.6 | 0 |  | 8.6806 | 750
| 3045 | 2760 | 5805 | 0 | 0 | 82 | 5723 | 110 | 71.65 | 62.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 19 |  |  | 84.3419 | 7620.6452 | 41.399 | 3099.3677 | 3120 | 62441.3298 | 58757.5 | 10.1219 | 85.6246 | 59159.01 | 563.8298 | 3942.3198 | 660 |  | 21.9375 | 58757.5