## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 570 | 0 | 570 | 0 | 0 | 2 | 570 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 1 | 85.05 | 9320 | 41.8 | 3568.5 | 960 | 6660 | 5700 | 10 | 85.2427 | 6405 | 0 | 255 | 0 |  | 65.9722 | 5700
2 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 55 | 11.15 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 2 | 85.25 | 9800 | 41.9 | 3685.5 | 480 | 6115 | 5635 | 9.8 | 86.5802 | 5850 | 0 | 265 | 0 |  | 65.2199 | 5635
3 | 620 | 0 | 620 | 0 | 0 | 2 | 620 | 55 | 11.75 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 3 | 84.9 | 8960 | 41.92 | 3708.9 | -840 | 5360 | 6200 | 10 | 85.5408 | 5117.3 | 0 | 242.7 | 0 |  | 71.7593 | 6200
4 | 515 | 0 | 515 | 0 | 0 | 3 | 515 | 54 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 4 | 85.1 | 9440 | 41.73 | 3486.6 | 480 | 5578.5 | 5098.5 | 9.9 | 86.0039 | 5340 | 0 | 238.5 | 0 |  | 59.0104 | 5098.5
5 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 55 | 9.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 84.55 | 8120 | 41.71 | 3463.2 | -1320 | 5828.3723 | 5100.5 | 10.1 | 85.3905 | 5768.16 | 2047.8723 | 60.2123 | 0 |  | 59.0336 | 5100.5
6 | 520 | 0 | 520 | 0 | 0 | 2 | 520 | 55 | 9.8 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 83.75 | 6200 | 41.92 | 3708.9 | -1920 | 8520.172 | 5252 | 10.1 | 87.0267 | 8477 | 5188.172 | 103.172 | 60 |  | 60.787 | 5252
7 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 13.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.6 | 8240 | 42.07 | 3884.4 | 2040 | 8623.5 | 6583.5 | 9.9 | 87.0133 | 8354.72 | 0 | 268.78 | 0 |  | 76.1979 | 6583.5
8 | 555 | 0 | 555 | 0 | 0 | 2 | 555 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 8 | 84.75 | 8600 | 41.85 | 3627 | 360 | 7680.5259 | 5605.5 | 10.1 | 84.991 | 7414.8 | 1715.0259 | 265.7259 | 0 |  | 64.8785 | 5605.5
9 | 435 | 0 | 435 | 0 | 0 | 3 | 435 | 50 | 9 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.7 | 8480 | 41.7 | 3451.5 | -120 | 7938.3936 | 4393.5 | 10.1 | 85.0905 | 7832.9 | 3664.8936 | 165.4936 | 60 |  | 50.8507 | 4393.5
10 | 200 | 240 | 440 | 0 | 0 | 3 | 440 | 50 | 4 | 6.45 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 1 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.95 | 9080 | 41.57 | 3299.4 | 600 | 8431.4346 | 4444 | 10.1 | 84.5953 | 8329.3 | 3387.4346 | 102.1346 | 0 |  | 51.4352 | 4444
11 | 455 | 360 | 815 | 0 | 0 | 4 | 815 | 100 | 10.15 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 85.4 | 10160 | 41.9 | 3685.5 | 1080 | 11684.557 | 8231.5 | 10.1 | 83.7181 | 11632.5 | 2373.057 | 52.057 | 0 |  | 95.272 | 8231.5
12 | 205 | 245 | 450 | 0 | 0 | 3 | 450 | 55 | 4.55 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.9 | 8960 | 41.95 | 3744 | -1200 | 3345 | 4545 | 10.1 | 84.6939 | 3082.5 | 0 | 262.5 | 0 |  | 52.6042 | 4545
13 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 50 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.15 | 9560 | 42 | 3802.5 | 600 | 5000 | 4400 | 10 | 85.0452 | 4666.4 | 0 | 333.6 | 0 |  | 50.9259 | 4400
14 | 20 | 490 | 510 | 0 | 0 | 3 | 510 | 85 | 0.55 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.2 | 7280 | 41.75 | 3510 | -2280 | 6722.0638 | 5151 | 10.1 | 86.0987 | 6745.2 | 3851.0638 | 36.8638 | 60 |  | 59.6181 | 5151
15 | 460 | 0 | 460 | 0 | 0 | 4 | 460 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.7 | 6080 | 42.1 | 3919.5 | -1200 | 4520.4681 | 4646 | 10.1 | 87.1311 | 4482.2 | 1074.4681 | 68.2681 | 30 |  | 53.7731 | 4646
16 | 135 | 440 | 575 | 0 | 0 | 3 | 575 | 110 | 12.7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.1 | 7040 | 41.91 | 3697.2 | 960 | 6767.5 | 5807.5 | 10.1 | 86.3032 | 6585.6 | 0 | 181.9 | 0 |  | 67.2164 | 5807.5
17 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.2 | 7280 | 41.7 | 3451.5 | 240 | 4790 | 4550 | 10 | 86.9597 | 4681.6 | 0 | 108.4 | 0 |  | 52.662 | 4550
18 | 20 | 445 | 465 | 0 | 0 | 3 | 465 | 70 | 0.3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.25 | 7400 | 41.7 | 3451.5 | 120 | 4770 | 4650 | 10 | 86.8568 | 4527.6 | 0 | 242.4 | 0 |  | 53.8194 | 4650
19 | 340 | 110 | 450 | 0 | 0 | 4 | 450 | 100 | 6.5 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.35 | 7640 | 41.5 | 3217.5 | 240 | 4740 | 4500 | 10 | 86.6517 | 4595.4 | 0 | 144.6 | 0 |  | 52.0833 | 4500
20 | 0 | 460 | 460 | 0 | 0 | 3 | 460 | 50 | 0 | 9.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.95 | 6680 | 41.5 | 3217.5 | -960 | 3686 | 4646 | 10.1 | 86.6118 | 3706.2 | 0 | 39.8 | 60 |  | 53.7731 | 4646
21 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 50 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.15 | 7160 | 41.5 | 3217.5 | 480 | 5030 | 4550 | 10 | 87.0629 | 4787.8 | 0 | 242.2 | 0 |  | 52.662 | 4550
22 | 40 | 445 | 485 | 0 | 0 | 3 | 485 | 90 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.4 | 7760 | 41.65 | 3393 | 600 | 6550.5833 | 4898.5 | 10.1 | 85.6926 | 6416.55 | 1052.0833 | 134.0333 | 0 |  | 56.6956 | 4898.5
23 | 475 | 215 | 690 | 0 | 0 | 4 | 690 | 110 | 10.85 | 5.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.65 | 8360 | 41.84 | 3615.3 | 600 | 7500 | 6900 | 10 | 86.0422 | 7368.05 | 0 | 131.95 | 0 |  | 79.8611 | 6900
24 | 25 | 585 | 610 | 0 | 0 | 3 | 610 | 70 | 0.25 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 85 | 9200 | 41.74 | 3498.3 | 840 | 6940 | 6100 | 10 | 85.3419 | 6606.5 | 0 | 333.5 | 0 |  | 70.6019 | 6100
25 | 630 | 195 | 825 | 0 | 0 | 3 | 825 | 80 | 13.65 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.55 | 8120 | 41.65 | 3393 | -1080 | 7252.5 | 8332.5 | 10.1 | 85.3905 | 7234.3 | 0 | 78.2 | 60 |  | 96.441 | 8332.5
26 | 75 | 655 | 730 | 0 | 0 | 4 | 730 | 89 | 2 | 12.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.3 | 7520 | 41.9 | 3685.5 | -600 | 6773 | 7373 | 10.1 | 85.8952 | 6759.8 | 0 | 73.2 | 60 |  | 85.3356 | 7373
27 | 490 | 230 | 720 | 0 | 0 | 3 | 720 | 110 | 9.95 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84 | 6800 | 41.97 | 3767.4 | -720 | 6552 | 7272 | 10.1 | 86.5087 | 6461 | 0 | 151 | 60 |  | 84.1667 | 7272
28 | 295 | 580 | 875 | 0 | 0 | 3 | 875 | 90 | 8.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 28 | 84.4 | 7760 | 41.96 | 3755.7 | 960 | 9797.5 | 8837.5 | 10.1 | 85.6926 | 9803.9 | 0 | 53.6 | 60 |  | 102.2859 | 8837.5
29 | 675 | 30 | 705 | 0 | 0 | 4 | 705 | 105 | 12.45 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.8 | 8720 | 41.85 | 3627 | 960 | 8080.5 | 7120.5 | 10.1 | 84.8917 | 7861 | 0 | 219.5 | 0 |  | 82.4132 | 7120.5
30 | 130 | 555 | 685 | 0 | 0 | 0 | 685 | 110 | 2.38 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 85.1 | 9440 | 42 | 3802.5 | 720 | 7638.5 | 6918.5 | 10.1 | 84.3008 | 7515.12 | 0 | 123.38 | 0 |  | 80.0752 | 6918.5
| 10980 | 6280 | 17260 | 0 | 0 | 89 | 17171 | 110 | 223.83 | 131.6 | 0 | 0 | 0 | 0 | 233.5 | 0 | 0 | 0 | 50 | 27 |  |  | 84.5717 | 8172 | 41.808 | 3577.86 | 1080 | 198876.0707 | 173442 | 10.0488 | 85.7821 | 194408.4 | 24354.0707 | 4977.6707 | 510 |  | 66.9144 | 173442