## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 740 | 0 | 740 | 0 | 0 | 6 | 740 | 54 | 13.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.95 | 9080 | 41.94 | 3732.3 | -360 | 7114 | 7474 | 10.1 | 84.5953 | 6660.3 | 0 | 453.7 | 0 |  | 86.5046 | 7474
2 | 340 | 365 | 705 | 0 | 0 | 4 | 705 | 55 | 6.4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.8 | 8720 | 42.01 | 3814.2 | -360 | 6760.5 | 7120.5 | 10.1 | 84.8917 | 6681.1 | 0 | 79.4 | 0 |  | 82.4132 | 7120.5
3 | 630 | 30 | 660 | 0 | 0 | 3 | 660 | 60 | 12 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.6 | 8240 | 41.68 | 3428.1 | -480 | 6186 | 6666 | 10.1 | 85.2903 | 5985.3 | 0 | 200.7 | 0 |  | 77.1528 | 6666
4 | 0 | 665 | 665 | 0 | 0 | 3 | 665 | 55 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.25 | 7400 | 41.89 | 3673.8 | -840 | 5876.5 | 6716.5 | 10.1 | 85.9968 | 5894.78 | 0 | 41.72 | 60 |  | 77.7373 | 6716.5
5 | 580 | 120 | 700 | 0 | 0 | 4 | 700 | 80 | 12.1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.1 | 9440 | 41.94 | 3732.3 | 2040 | 9110 | 7070 | 10.1 | 84.3008 | 8954.4 | 0 | 155.6 | 0 |  | 81.8287 | 7070
6 | 240 | 620 | 860 | 0 | 0 | 3 | 860 | 80 | 6.6 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.2 | 7280 | 42.09 | 3907.8 | -2160 | 6526 | 8686 | 10.1 | 86.0987 | 6514.2 | 0 | 71.8 | 60 |  | 100.5324 | 8686
7 | 670 | 0 | 670 | 0 | 0 | 3 | 670 | 55 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.7 | 8480 | 42.08 | 3896.1 | 1200 | 7900 | 6700 | 10 | 85.9415 | 7722.6 | 0 | 177.4 | 0 |  | 77.5463 | 6700
8 | 555 | 470 | 1025 | 0 | 0 | 0 | 1025 | 90 | 11.58 | 9.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84 | 6800 | 42.03 | 3837.6 | -1680 | 8672.5 | 10352.5 | 10.1 | 86.5087 | 8683.2 | 0 | 49.3 | 60 |  | 119.8206 | 10352.5
9 | 370 | 325 | 695 | 0 | 0 | 7 | 695 | 55 | 6.99 | 5.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.9 | 6560 | 42 | 3802.5 | -240 | 6779.5 | 7019.5 | 10.1 | 86.7152 | 6718.74 | 0 | 60.76 | 0 |  | 81.2442 | 7019.5
10 | 290 | 435 | 725 | 0 | 0 | 3 | 725 | 90 | 5.51 | 8.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 42 | 3802.5 | -240 | 7082.5 | 7322.5 | 10.1 | 86.9226 | 7094.12 | 0 | 48.38 | 60 |  | 84.7512 | 7322.5
11 | 720 | 0 | 720 | 0 | 0 | 4 | 720 | 55 | 14.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.2 | 7280 | 42.05 | 3861 | 960 | 8124 | 7164 | 9.95 | 87.3967 | 7923.3 | 0 | 200.7 | 0 |  | 82.9167 | 7164
12 | 20 | 740 | 760 | 0 | 0 | 3 | 760 | 110 | 0.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 84.3 | 7520 | 42 | 3802.5 | 240 | 7916 | 7676 | 10.1 | 85.8952 | 7829.25 | 0 | 146.75 | 60 |  | 88.8426 | 7676
13 | 735 | 0 | 735 | 0 | 0 | 3 | 735 | 55 | 14.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.4 | 7760 | 41.96 | 3755.7 | 240 | 7663.5 | 7423.5 | 10.1 | 85.6926 | 7497.1 | 0 | 166.4 | 0 |  | 85.9201 | 7423.5
14 | 30 | 895 | 925 | 0 | 0 | 3 | 925 | 75 | 0.43 | 16.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.45 | 7880 | 42 | 3802.5 | 120 | 9277.5 | 9157.5 | 9.9 | 87.3208 | 9050.24 | 0 | 227.26 | 0 |  | 105.9896 | 9157.5
15 | 735 | 0 | 735 | 0 | 0 | 3 | 735 | 55 | 14.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.55 | 8120 | 41.93 | 3720.6 | 240 | 7663.5 | 7423.5 | 10.1 | 85.3905 | 7467.9 | 0 | 195.6 | 0 |  | 85.9201 | 7423.5
16 | 15 | 735 | 750 | 0 | 0 | 3 | 750 | 55 | 0.15 | 14.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Αποκατάσταση βλάβης Απ/Ζ 16 από ΑΔΜΗΕ | 16 | 84.8 | 8720 | 41.93 | 3720.6 | 600 | 8175 | 7575 | 10.1 | 84.8917 | 8108.1 | 0 | 126.9 | 60 |  | 87.6736 | 7575
17 | 425 | 775 | 1200 | 0 | 0 | 3 | 1200 | 100 | 8.3 | 15.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7040 | 41.9 | 3685.5 | -1680 | 10200 | 11880 | 9.9 | 88.0467 | 10088.6 | 0 | 111.4 | 0 |  | 137.5 | 11880
18 | 0 | 740 | 740 | 0 | 0 | 3 | 740 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.35 | 7640 | 42.07 | 3884.4 | 600 | 8074 | 7474 | 10.1 | 85.7938 | 8087.76 | 0 | 46.24 | 60 |  | 86.5046 | 7474
19 | 760 | 0 | 760 | 0 | 0 | 3 | 760 | 55 | 14.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 85 | 9200 | 42 | 3802.5 | 1560 | 9160 | 7600 | 10 | 85.3419 | 9030.1 | 0 | 129.9 | 0 |  | 87.963 | 7600
20 | 80 | 715 | 795 | 0 | 0 | 3 | 795 | 80 | 2.08 | 14.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.95 | 9080 | 42.05 | 3861 | -120 | 7830 | 7950 | 10 | 85.4412 | 7453.3 | 0 | 376.7 | 0 |  | 92.0139 | 7950
21 | 675 | 115 | 790 | 0 | 0 | 3 | 790 | 70 | 15.95 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.75 | 8600 | 42.05 | 3861 | -480 | 7459.5 | 7939.5 | 10.05 | 85.4139 | 7444.4 | 0 | 15.1 | 0 |  | 91.8924 | 7939.5
22 | 40 | 810 | 850 | 0 | 0 | 3 | 850 | 70 | 0.55 | 15.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.35 | 7640 | 42 | 3802.5 | -960 | 7625 | 8585 | 10.1 | 85.7938 | 7539.6 | 0 | 85.4 | 0 |  | 99.3634 | 8585
23 | 750 | 0 | 750 | 0 | 0 | 3 | 750 | 55 | 16.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.45 | 7880 | 42.05 | 3861 | 240 | 7815 | 7575 | 10.1 | 85.5917 | 7587.78 | 0 | 227.22 | 0 |  | 87.6736 | 7575
24 | 0 | 715 | 715 | 0 | 0 | 3 | 715 | 55 | 0 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.35 | 7640 | 42.05 | 3861 | -240 | 6981.5 | 7221.5 | 10.1 | 85.7938 | 6956 | 0 | 25.5 | 0 |  | 83.5822 | 7221.5
25 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.05 | 6920 | 42.05 | 3861 | -720 | 6350 | 7070 | 10.1 | 86.4059 | 6336.4 | 0 | 73.6 | 60 |  | 81.8287 | 7070
26 | 0 | 710 | 710 | 0 | 0 | 3 | 710 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 83.9 | 6560 | 42.05 | 3861 | -360 | 6811 | 7171 | 10.1 | 86.7152 | 6716 | 0 | 95 | 0 |  | 82.9977 | 7171
27 | 720 | 0 | 720 | 0 | 0 | 3 | 720 | 55 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 83.75 | 6200 | 42.05 | 3861 | -360 | 6912 | 7272 | 10.1 | 87.0267 | 6921.53 | 0 | 50.47 | 60 |  | 84.1667 | 7272
28 | 0 | 705 | 705 | 0 | 0 | 3 | 705 | 55 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.7 | 6080 | 41.91 | 3697.2 | -120 | 7000.5 | 7120.5 | 10.1 | 87.1311 | 7066.4 | 0 | 34.1 | 100 |  | 82.4132 | 7120.5
29 | 655 | 115 | 770 | 0 | 0 | 3 | 770 | 70 | 14 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.9 | 6560 | 42.05 | 3861 | 480 | 12737.973 | 8085 | 10.5 | 83.4118 | 12789 | 4172.973 | 18.973 | 70 |  | 93.5764 | 8085
30 | 175 | 675 | 850 | 0 | 0 | 2 | 850 | 85 | 4.5 | 13.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.2 | 7280 | 42 | 3802.5 | 720 | 11060.3191 | 8585 | 10.1 | 86.0987 | 10934.55 | 1755.3191 | 125.7691 | 0 |  | 99.3634 | 8585
31 | 750 | 0 | 750 | 0 | 0 | 3 | 750 | 55 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.3 | 7520 | 42.02 | 3825.9 | 240 | 7740 | 7500 | 10 | 86.7541 | 7599.8 | 0 | 140.2 | 0 |  | 86.8056 | 7500
| 12400 | 11475 | 23875 | 0 | 0 | 99 | 23776 | 110 | 245.57 | 226.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 34 |  |  | 84.3581 | 7659.3548 | 41.9945 | 3796.0839 | -1920 | 244583.7921 | 240575.5 | 10.0765 | 85.9778 | 241335.85 | 5928.2921 | 3957.9421 | 710 |  | 89.8206 | 240575.5