## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 135 | 605 | 740 | 0 | 0 | 4 | 740 | 109 | 2.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 83.85 | 6440 | 41.92 | 3708.9 | -1080 | 6394 | 7474 | 10.1 | 86.8188 | 6356.6 | 0 | 97.4 | 60 |  | 86.5046 | 7474
2 | 170 | 690 | 860 | 0 | 0 | 2 | 860 | 90 | 4.6 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 83.35 | 5240 | 41.96 | 3755.7 | -1200 | 7916 | 9116 | 10.6 | 83.7238 | 7931.25 | 0 | 104.75 | 120 |  | 105.5093 | 9116
3 | 720 | 345 | 1065 | 0 | 0 | 3 | 1065 | 110 | 14 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.7 | 8480 | 41.93 | 3720.6 | 3240 | 13996.5 | 10756.5 | 10.1 | 85.0905 | 13862.7 | 0 | 133.8 | 0 |  | 124.4965 | 10756.5
4 | 445 | 930 | 1375 | 0 | 0 | 3 | 1375 | 110 | 10.5 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 83.5 | 5600 | 42 | 3802.5 | -2880 | 11530 | 14410 | 10.48 | 84.3764 | 11523.3 | 0 | 66.7 | 60 |  | 166.7824 | 14410
5 | 600 | 265 | 865 | 0 | 0 | 3 | 865 | 110 | 12.2 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 5 | 83.75 | 6200 | 41.9 | 3685.5 | 600 | 9336.5 | 8736.5 | 10.1 | 87.0267 | 9081.2 | 0 | 255.3 | 0 |  | 101.1169 | 8736.5
6 | 0 | 645 | 645 | 0 | 0 | 3 | 645 | 55 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.15 | 7160 | 41.9 | 3685.5 | 960 | 10233.4641 | 6837 | 10.6 | 82.1348 | 10267.4 | 2436.4641 | 66.0641 | 100 |  | 79.1319 | 6837
7 | 650 | 0 | 650 | 0 | 0 | 3 | 650 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 7 | 84.4 | 7760 | 41.88 | 3662.1 | 600 | 9443.9474 | 6565 | 10.1 | 85.6926 | 9301.8 | 2278.9474 | 142.1474 | 0 |  | 75.9838 | 6565
8 | 0 | 745 | 745 | 0 | 0 | 3 | 745 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7040 | 42.01 | 3814.2 | -720 | 6804.5 | 7524.5 | 10.1 | 86.3032 | 6717.6 | 0 | 86.9 | 0 |  | 87.0891 | 7524.5
9 | 590 | 115 | 705 | 0 | 0 | 3 | 705 | 70 | 14 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 85 | 9200 | 41.98 | 3779.1 | 2160 | 9280.5 | 7120.5 | 10.1 | 84.4969 | 9173.58 | 0 | 106.92 | 0 |  | 82.4132 | 7120.5
10 | 245 | 645 | 890 | 0 | 0 | 3 | 890 | 110 | 6.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.1 | 9440 | 41.96 | 3755.7 | 240 | 10622.7824 | 8989 | 10.1 | 84.3008 | 10552.4 | 1393.7824 | 70.3824 | 0 |  | 104.0394 | 8989
11 | 630 | 275 | 905 | 0 | 0 | 3 | 905 | 104 | 14.77 | 7.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.6 | 8240 | 41.77 | 3533.4 | -1200 | 7804.75 | 9004.75 | 9.95 | 86.5761 | 7561.56 | 0 | 243.19 | 0 |  | 104.2216 | 9004.75
12 | 0 | 580 | 580 | 0 | 0 | 3 | 580 | 55 | 0 | 11.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 12 | 83.9 | 6560 | 41.45 | 3159 | -1680 | 7548.9677 | 5858 | 10.1 | 86.7152 | 7581 | 3370.9677 | 27.9677 | 60 |  | 67.8009 | 5858
13 | 625 | 0 | 625 | 0 | 0 | 2 | 625 | 55 | 11.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.05 | 6920 | 41.83 | 3603.6 | 360 | 10151.2234 | 6312.5 | 10.1 | 86.4059 | 10257.52 | 3478.7234 | 13.7034 | 120 |  | 73.0613 | 6312.5
14 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 55 | 0 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.85 | 8840 | 41.75 | 3510 | 1920 | 8270 | 6350 | 10 | 85.6406 | 8187.55 | 0 | 82.45 | 0 |  | 73.4954 | 6350
15 | 0 | 630 | 630 | 0 | 0 | 3 | 630 | 55 | 0 | 12.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.65 | 8360 | 41.69 | 3439.8 | -480 | 5883 | 6363 | 10.1 | 85.1903 | 5848.68 | 0 | 34.32 | 0 |  | 73.6458 | 6363
16 | 45 | 650 | 695 | 0 | 0 | 3 | 695 | 80 | 1.05 | 12.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.15 | 7160 | 41.98 | 3779.1 | -1200 | 9597.1489 | 7228 | 10.4 | 83.7143 | 9709.7 | 3569.1489 | 7.4489 | 120 |  | 83.6574 | 7228
17 | 415 | 145 | 560 | 0 | 0 | 3 | 560 | 54 | 8.1 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.7 | 8480 | 41.33 | 3018.6 | 1320 | 6864 | 5544 | 9.9 | 86.8095 | 6587.52 | 0 | 276.48 | 0 |  | 64.1667 | 5544
18 | 0 | 790 | 790 | 0 | 0 | 3 | 790 | 55 | 0 | 15.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84 | 6800 | 41.85 | 3627 | -1680 | 6220 | 7900 | 10 | 87.3738 | 5977.5 | 0 | 242.5 | 0 |  | 91.4352 | 7900
19 | 695 | 0 | 695 | 0 | 0 | 3 | 695 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.15 | 7160 | 42.05 | 3861 | 360 | 7379.5 | 7019.5 | 10.1 | 86.2009 | 7326 | 0 | 53.5 | 0 |  | 81.2442 | 7019.5
20 | 0 | 700 | 700 | 0 | 0 | 3 | 700 | 55 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 83.75 | 6200 | 42.02 | 3825.9 | -960 | 6110 | 7070 | 10.1 | 87.0267 | 6097.5 | 0 | 12.5 | 0 |  | 81.8287 | 7070
21 | 690 | 0 | 690 | 0 | 0 | 3 | 690 | 55 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 82.45 | 3190 | 41.92 | 3708.9 | -3010 | 4338.5 | 7348.5 | 10.65 | 85.1849 | 4312 | 0 | 86.5 | 60 |  | 85.0521 | 7348.5
22 | 0 | 605 | 605 | 0 | 0 | 2 | 605 | 55 | 0 | 11.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 81.9 | 1980 | 41.76 | 3521.7 | -1210 | 5750.8723 | 6413 | 10.6 | 86.7664 | 5817 | 547.8723 | 33.8723 | 100 |  | 74.2245 | 6413
23 | 685 | 0 | 685 | 0 | 0 | 3 | 685 | 55 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 82.05 | 2310 | 42 | 3802.5 | 330 | 7728 | 7398 | 10.8 | 84.8407 | 7797.9 | 0 | 10.1 | 80 |  | 85.625 | 7398
24 | 0 | 550 | 550 | 0 | 0 | 3 | 550 | 54 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 82.6 | 3520 | 41.92 | 3708.9 | 1210 | 6957.5 | 5747.5 | 10.45 | 86.4944 | 6986.4 | 0 | 31.1 | 60 |  | 66.522 | 5747.5
25 | 560 | 0 | 560 | 0 | 0 | 3 | 560 | 55 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 82.6 | 3520 | 41.88 | 3662.1 | 0 | 5852 | 5852 | 10.45 | 86.4944 | 5876.5 | 0 | 35.5 | 60 |  | 67.7315 | 5852
26 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 82.6 | 3520 | 41.9 | 3685.5 | 0 | 5951.25 | 5951.25 | 10.35 | 87.3301 | 5934.9 | 0 | 16.35 | 0 |  | 68.8802 | 5951.25
27 | 560 | 0 | 560 | 0 | 0 | 3 | 560 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 82.8 | 3960 | 41.84 | 3615.3 | 440 | 6096 | 5656 | 10.1 | 89.0531 | 6071.1 | 0 | 84.9 | 60 |  | 65.463 | 5656
28 | 80 | 480 | 560 | 0 | 0 | 2 | 560 | 80 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 82.6 | 3520 | 41.72 | 3474.9 | -440 | 5216 | 5656 | 10.1 | 89.4918 | 5247.44 | 0 | 28.56 | 60 |  | 65.463 | 5656
29 | 505 | 0 | 505 | 0 | 0 | 0 | 505 | 50 | 10.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 82.6 | 3520 | 41.48 | 3194.1 | 0 | 5226.75 | 5226.75 | 10.35 | 87.3301 | 5204.9 | 0 | 81.85 | 60 |  | 60.4948 | 5226.75
30 | 0 | 505 | 505 | 0 | 0 | 6 | 505 | 51 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 82.7 | 3740 | 41.33 | 3018.6 | 220 | 5320.5 | 5100.5 | 10.1 | 89.2719 | 5226.8 | 0 | 93.7 | 0 |  | 59.0336 | 5100.5
31 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 55 | 9.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 83.35 | 5240 | 41.7 | 3451.5 | 1500 | 6450 | 4950 | 10 | 88.7473 | 6274.5 | 0 | 175.5 | 0 |  | 57.2917 | 4950
| 9540 | 12105 | 21645 | 0 | 0 | 90 | 21555 | 110 | 195.4 | 242.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 34 |  |  | 83.6435 | 5977.4194 | 41.8261 | 3599.071 | -2280 | 236274.1563 | 221478.25 | 10.2323 | 86.1211 | 234651.8 | 17075.9063 | 2802.3563 | 1180 |  | 82.6905 | 221478.25