## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 480 | 0 | 480 | 0 | 0 | 3 | 480 | 55 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 83.2 | 4880 | 41.71 | 3463.2 | -360 | 4488 | 4848 | 10.1 | 88.1885 | 4453 | 0 | 95 | 60 |  | 56.1111 | 4848
2 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 50 | 0 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 83.2 | 4880 | 41.57 | 3299.4 | 0 | 4444 | 4444 | 10.1 | 88.1885 | 4462.64 | 0 | 41.36 | 60 |  | 51.4352 | 4444
3 | 455 | 30 | 485 | 0 | 0 | 2 | 485 | 80 | 9.1 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 83.3 | 5120 | 41.76 | 3521.7 | 240 | 5138.5 | 4898.5 | 10.1 | 87.975 | 5102.7 | 0 | 95.8 | 60 |  | 56.6956 | 4898.5
4 | 0 | 430 | 430 | 0 | 0 | 3 | 430 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 83.1 | 4640 | 41.75 | 3510 | -480 | 3863 | 4343 | 10.1 | 88.4031 | 3876.6 | 0 | 46.4 | 60 |  | 50.2662 | 4343
5 | 390 | 0 | 390 | 0 | 0 | 3 | 390 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.1 | 4640 | 41.65 | 3393 | 0 | 3939 | 3939 | 10.1 | 88.4031 | 3911.05 | 0 | 87.95 | 60 |  | 45.5903 | 3939
6 | 45 | 380 | 425 | 0 | 0 | 3 | 425 | 90 | 0.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 82.9 | 4180 | 41.7 | 3451.5 | -460 | 3832.5 | 4292.5 | 10.1 | 88.8354 | 3822 | 0 | 70.5 | 60 |  | 49.6817 | 4292.5
7 | 340 | 0 | 340 | 0 | 0 | 0 | 340 | 45 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82.9 | 4180 | 41.66 | 3404.7 | 0 | 3434 | 3434 | 10.1 | 88.8354 | 3384 | 0 | 110 | 60 |  | 39.7454 | 3434
8 | 45 | 520 | 565 | 0 | 0 | 0 | 565 | 110 | 0.79 | 11.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 83.1 | 4640 | 41.59 | 3322.8 | 460 | 6166.5 | 5706.5 | 10.1 | 88.4031 | 6230 | 0 | 36.5 | 100 |  | 66.0475 | 5706.5
9 | 340 | 0 | 340 | 0 | 0 | 8 | 340 | 55 | 8.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 83.55 | 5720 | 41.49 | 3205.8 | 1080 | 4446 | 3366 | 9.9 | 89.2122 | 4335 | 0 | 111 | 0 |  | 38.9583 | 3366
10 | 0 | 345 | 345 | 0 | 0 | 3 | 345 | 50 | 0 | 8.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.5 | 5600 | 41.56 | 3287.7 | -120 | 3364.5 | 3484.5 | 10.1 | 87.551 | 3452.9 | 0 | 11.6 | 100 |  | 40.3299 | 3484.5
11 | 160 | 135 | 295 | 0 | 0 | 3 | 295 | 85 | 3.25 | 2.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 83.65 | 5960 | 41.43 | 3135.6 | 360 | 3310 | 2950 | 10 | 88.108 | 3045 | 0 | 265 | 0 |  | 34.1435 | 2950
12 | 0 | 300 | 300 | 0 | 0 | 3 | 300 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.7 | 6080 | 41.34 | 3030.3 | 120 | 3150 | 3030 | 10.1 | 87.1311 | 3069.4 | 0 | 80.6 | 0 |  | 35.0694 | 3030
13 | 310 | 0 | 310 | 0 | 0 | 2 | 310 | 50 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.8 | 6320 | 41.3 | 2983.5 | 240 | 3371 | 3131 | 10.1 | 86.9226 | 3291.8 | 0 | 79.2 | 0 |  | 36.2384 | 3131
14 | 0 | 275 | 275 | 0 | 0 | 3 | 275 | 50 | 0 | 5.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.9 | 6560 | 41.52 | 3240.9 | 240 | 3141.25 | 2901.25 | 10.55 | 83.0164 | 2854.3 | 0 | 286.95 | 0 |  | 33.5793 | 2901.25
15 | 150 | 140 | 290 | 0 | 0 | 3 | 290 | 50 | 3.1 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83.9 | 6560 | 41.75 | 3510 | 0 | 2929 | 2929 | 10.1 | 86.7152 | 2890.8 | 0 | 98.2 | 60 |  | 33.9005 | 2929
16 | 20 | 330 | 350 | 0 | 0 | 3 | 350 | 65 | 0.5 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 16 | 83.9 | 6560 | 41.76 | 3521.7 | 0 | 3535 | 3535 | 10.1 | 86.7152 | 3460.2 | 0 | 134.8 | 60 |  | 40.9144 | 3535
17 | 295 | 0 | 295 | 0 | 0 | 0 | 295 | 50 | 6.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84 | 6800 | 41.82 | 3591.9 | 240 | 3219.5 | 2979.5 | 10.1 | 86.5087 | 3080.6 | 0 | 198.9 | 60 |  | 34.485 | 2979.5
18 | 80 | 230 | 310 | 0 | 0 | 0 | 310 | 94 | 2.01 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 83.55 | 5720 | 41.69 | 3439.8 | -1080 | 2128.5 | 3208.5 | 10.35 | 85.3334 | 2191 | 0 | 37.5 | 100 |  | 37.1354 | 3208.5
19 | 375 | 40 | 415 | 0 | 0 | 8 | 415 | 94 | 8.15 | 1.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 19 | 83.85 | 6440 | 41.64 | 3381.3 | 720 | 4911.5 | 4191.5 | 10.1 | 86.8188 | 4883.7 | 0 | 87.8 | 60 |  | 48.5127 | 4191.5
20 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 50 | 0 | 5.16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 20 | 83.85 | 6440 | 41.41 | 3112.2 | 0 | 2373.5 | 2373.5 | 10.1 | 86.8188 | 2378.5 | 0 | 55 | 60 |  | 27.4711 | 2373.5
21 | 0 | 265 | 265 | 0 | 0 | 2 | 265 | 54 | 0 | 5.41 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 21 | 83.85 | 6440 | 41.56 | 3287.7 | 0 | 2769.25 | 2769.25 | 10.45 | 83.911 | 2841.6 | 0 | 27.65 | 100 |  | 32.0515 | 2769.25
22 | 0 | 230 | 230 | 0 | 0 | 2 | 230 | 46 | 0 | 4.96 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 22 | 84 | 6800 | 41.42 | 3123.9 | 360 | 2625.5 | 2265.5 | 9.85 | 88.7044 | 2307.9 | 0 | 317.6 | 0 |  | 26.2211 | 2265.5
23 | 0 | 240 | 240 | 0 | 0 | 3 | 240 | 46 | 0 | 5.4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 23 | 84 | 6800 | 41.46 | 3170.7 | 0 | 2424 | 2424 | 10.1 | 86.5087 | 2365.2 | 0 | 58.8 | 0 |  | 28.0556 | 2424
24 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 5.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 24 | 83.95 | 6680 | 41.54 | 3264.3 | -120 | 2405.95 | 2525.95 | 10.31 | 84.8477 | 2284.9 | 0 | 121.05 | 0 |  | 29.2355 | 2525.95
25 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 25 | 84.2 | 7280 | 41.41 | 3112.2 | 600 | 4150.2766 | 2279 | 10.6 | 82.0375 | 4103.8 | 1271.2766 | 106.4766 | 60 |  | 26.3773 | 2279
26 | 0 | 240 | 240 | 0 | 0 | 2 | 240 | 54 | 0 | 4.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 26 | 84.25 | 7400 | 41.54 | 3264.3 | 120 | 3650.383 | 2424 | 10.1 | 85.9968 | 3636 | 1106.383 | 74.383 | 60 |  | 28.0556 | 2424
27 | 0 | 210 | 210 | 0 | 0 | 3 | 210 | 54 | 0 | 4.15 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 27 | 84.35 | 7640 | 41.42 | 3123.9 | 240 | 4111 | 2121 | 10.1 | 85.7938 | 3905.5 | 1750 | 205.5 | 0 |  | 24.5486 | 2121
28 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 28 | 84.25 | 7400 | 41.3 | 2983.5 | -240 | 4869.8399 | 2162.75 | 10.55 | 82.3287 | 4870.6 | 2947.0899 | 59.2399 | 60 |  | 25.0318 | 2162.75
29 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4.2 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 29 | 84.3 | 7520 | 41.16 | 2819.7 | 120 | 4012.2766 | 2121 | 10.1 | 85.8952 | 3942 | 1771.2766 | 130.2766 | 60 |  | 24.5486 | 2121
30 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 30 | 84.35 | 7640 | 41.19 | 2854.8 | 120 | 2291.5 | 2171.5 | 10.1 | 85.7938 | 2197.75 | 0 | 153.75 | 60 |  | 25.1331 | 2171.5
| 3485 | 6105 | 9590 | 0 | 0 | 81 | 9509 | 110 | 75.1 | 129 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 45 |  |  | 83.715 | 6117.3333 | 41.5367 | 3260.4 | 2400 | 108495.2261 | 97249.2 | 10.1407 | 86.7503 | 106630.44 | 8846.0261 | 3284.7861 | 1420 |  | 37.519 | 97249.2