## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 84.45 | 7880 | 41.14 | 2796.3 | 240 | 2340 | 2100 | 10 | 86.4476 | 2184.42 | 0 | 155.58 | 0 |  | 24.3056 | 2100
2 | 0 | 190 | 190 | 0 | 0 | 2 | 190 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 84.45 | 7880 | 40.99 | 2620.8 | 0 | 2437.1566 | 1871.5 | 9.85 | 87.764 | 2166 | 565.6566 | 271.1566 | 0 |  | 21.6609 | 1871.5
3 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 83.2 | 4880 | 40.97 | 2597.4 | -3000 | 3655.9459 | 2110 | 10.55 | 84.4269 | 3759 | 4545.9459 | 16.9459 | 120 |  | 24.4213 | 2110
4 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.2 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 4 | 83.9 | 6560 | 41.12 | 2772.9 | 1680 | 4490.3564 | 2225.25 | 10.35 | 84.6206 | 4416.5 | 585.1064 | 133.8564 | 60 |  | 25.7552 | 2225.25
5 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 50 | 0 | 4.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 5 | 83.9 | 6560 | 41.23 | 2901.6 | 0 | 2111.5 | 2111.5 | 10.3 | 85.0314 | 2123.8 | 0 | 47.7 | 60 |  | 24.4387 | 2111.5
6 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4.05 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 6 | 84 | 6800 | 41.33 | 3018.6 | 240 | 4451.8613 | 2070.5 | 10.1 | 86.5087 | 4453 | 2141.3613 | 58.8613 | 60 |  | 23.9641 | 2070.5
7 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 54 | 0 | 4.05 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 7 | 84.05 | 6920 | 41.61 | 3346.2 | 120 | 2220 | 2100 | 10.5 | 83.1142 | 2102.4 | 0 | 177.6 | 60 |  | 24.3056 | 2100
8 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 8 | 84.25 | 7400 | 41.7 | 3451.5 | 480 | 5663.3085 | 2236.5 | 10.65 | 81.5557 | 5336.3 | 2946.8085 | 387.0085 | 60 |  | 25.8854 | 2236.5
9 | 45 | 130 | 175 | 0 | 0 | 3 | 175 | 80 | 1.8 | 2.45 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 9 | 84.3 | 7520 | 41.7 | 3451.5 | 120 | 1957.5 | 1837.5 | 10.5 | 82.623 | 1795.8 | 0 | 161.7 | 0 |  | 21.2674 | 1837.5
10 | 0 | 200 | 200 | 0 | 0 | 4 | 200 | 55 | 0 | 4.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 10 | 84.2 | 7280 | 41.63 | 3369.6 | -240 | 1780 | 2020 | 10.1 | 86.0987 | 1686.3 | 0 | 93.7 | 0 |  | 23.3796 | 2020
11 | 135 | 125 | 260 | 0 | 0 | 2 | 260 | 80 | 3.5 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 11 | 83.7 | 6080 | 41.66 | 3404.7 | -1200 | 5584.383 | 2678 | 10.3 | 85.4392 | 5387.4 | 4106.383 | 256.983 | 60 |  | 30.9954 | 2678
12 | 140 | 45 | 185 | 0 | 0 | 3 | 185 | 45 | 3.05 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0 | 2 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 12 | 83.8 | 6320 | 41.47 | 3182.4 | 240 | 2460.25 | 1970.25 | 10.65 | 82.4337 | 2502.63 | 250 | 57.62 | 100 |  | 22.8038 | 1970.25
13 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 45 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 13 | 84 | 6800 | 41.15 | 2808 | 480 | 3123.5691 | 888.25 | 10.45 | 83.6113 | 2883.5 | 1755.3191 | 240.0691 | 0 |  | 10.2807 | 888.25
14 | 65 | 0 | 65 | 0 | 0 | 2 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 14 | 84.1 | 7040 | 41.12 | 2772.9 | 240 | 2647.75 | 689 | 10.6 | 82.2323 | 2474.7 | 1718.75 | 173.05 | 0 |  | 7.9745 | 689
15 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 15 | 83.4 | 5360 | 41.1 | 2749.5 | -1680 | 844.4011 | 749 | 10.7 | 82.8412 | 693 | 1775.4011 | 211.4011 | 60 |  | 8.669 | 749
16 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 83.55 | 5720 | 41.79 | 3556.8 | 360 | 4377.5638 | 1666.5 | 10.1 | 87.4456 | 4399.2 | 2351.0638 | 38.3638 | 60 |  | 19.2882 | 1666.5
17 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 45 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.6 | 5840 | 41.76 | 3521.7 | 120 | 3408.2872 | 958.5 | 10.65 | 82.83 | 3266 | 2329.7872 | 202.2872 | 60 |  | 11.0938 | 958.5
18 | 325 | 250 | 575 | 0 | 0 | 3 | 575 | 80 | 8.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 83.55 | 5720 | 41.61 | 3346.2 | -120 | 8257.9255 | 6037.5 | 10.5 | 84.1144 | 8220.3 | 2340.4255 | 97.6255 | 60 |  | 69.8785 | 6037.5
19 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.2 | 7280 | 41.98 | 3779.1 | 1560 | 3640 | 2080 | 10.4 | 83.6151 | 3518.6 | 0 | 121.4 | 0 |  | 24.0741 | 2080
20 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 55 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.75 | 6200 | 41.7 | 3451.5 | -1080 | 2385.7826 | 1656 | 10.35 | 84.9246 | 2421.9 | 1809.7826 | 63.8826 | 100 |  | 19.1667 | 1656
21 | 90 | 25 | 115 | 0 | 0 | 2 | 115 | 79 | 2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.65 | 5960 | 41.67 | 3416.4 | -240 | 1555.087 | 1219 | 10.6 | 83.1208 | 1484 | 576.087 | 131.087 | 60 |  | 14.1088 | 1219
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.65 | 5960 | 41.6 | 3334.5 | 0 | 2664.8191 | 909.5 | 10.7 | 82.344 | 2591.5 | 1755.3191 | 73.3191 | 0 |  | 10.5266 | 909.5
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 54 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.95 | 6680 | 41.56 | 3287.7 | 720 | 1576 | 856 | 10.7 | 81.7551 | 1452.7 | 0 | 123.3 | 0 |  | 9.9074 | 856
24 | 20 | 110 | 130 | 0 | 0 | 3 | 130 | 70 | 0.5 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84 | 6800 | 41.68 | 3428.1 | 120 | 1433 | 1313 | 10.1 | 86.5087 | 1413.75 | 0 | 79.25 | 60 |  | 15.1968 | 1313
25 | 470 | 285 | 755 | 0 | 0 | 2 | 755 | 90 | 11.7 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 |  | 25 | 82.85 | 4070 | 41.09 | 2737.8 | -2730 | 5944.9202 | 7738.75 | 10.25 | 87.6425 | 5913.3 | 936.1702 | 91.6202 | 60 |  | 89.5689 | 7738.75
26 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 50 | 0 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.7 | 6080 | 41.2 | 2866.5 | 2010 | 2868.5 | 858.5 | 10.1 | 87.1311 | 2795.9 | 0 | 132.6 | 60 |  | 9.9363 | 858.5
27 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.65 | 5960 | 41.3 | 2983.5 | -120 | 847.5 | 967.5 | 10.75 | 81.961 | 759.2 | 0 | 148.3 | 60 |  | 11.1979 | 967.5
28 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.3 | 5120 | 41.32 | 3006.9 | -840 | 839.1489 | 860 | 10.75 | 82.6556 | 730 | 819.1489 | 109.1489 | 0 |  | 9.9537 | 860
29 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 29 | 83.55 | 5720 | 41.34 | 3030.3 | 600 | 3232.8077 | 940.5 | 10.45 | 84.5168 | 3197.4 | 1692.3077 | 65.4077 | 30 |  | 10.8854 | 940.5
30 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 54 | 0 | 2.15 | 0 | 0 | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 30 | 83 | 4400 | 41.52 | 3240.9 | -1320 | 1593.4435 | 1139.25 | 10.85 | 82.493 | 1666 | 1774.1935 | 27.4435 | 100 |  | 13.1858 | 1139.25
31 | 90 | 90 | 180 | 0 | 0 | 3 | 180 | 80 | 2.2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 82.5 | 3300 | 41.76 | 3521.7 | -1100 | 2606.2766 | 1935 | 10.75 | 84.2883 | 2569.6 | 1771.2766 | 96.6766 | 60 |  | 22.3958 | 1935
| 1960 | 3700 | 5660 | 0 | 0 | 84 | 5576 | 90 | 48.9 | 81.25 | 205 | 0 | 2.67 | 0 | 0 | 0 | 70.75 | 0 | 22 | 42 |  |  | 83.7468 | 6196.4516 | 41.4452 | 3153.3387 | -4340 | 92999.0442 | 58792.75 | 10.3874 | 84.6253 | 90364.1 | 38546.2942 | 4044.9442 | 1410 |  | 21.9507 | 58792.75