## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 82.45 | 3190 | 41.54 | 3264.3 | -110 | 750 | 860 | 10.75 | 84.3924 | 671.6 | 0 | 78.4 | 0 |  | 9.9537 | 860
2 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 54 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.45 | 5480 | 41.42 | 3123.9 | 2290 | 3150 | 860 | 10.75 | 82.3564 | 3044.1 | 0 | 165.9 | 60 |  | 9.9537 | 860
3 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.4 | 5360 | 41.25 | 2925 | -120 | 671.25 | 791.25 | 10.55 | 84.019 | 690 | 0 | 21.25 | 40 |  | 9.158 | 791.25
4 | 20 | 90 | 110 | 0 | 0 | 3 | 110 | 80 | 0.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 83.3 | 5120 | 41.44 | 3147.3 | -240 | 860 | 1100 | 10 | 88.8547 | 667.5 | 0 | 192.5 | 0 |  | 12.7315 | 1100
5 | 95 | 20 | 115 | 0 | 0 | 3 | 115 | 80 | 2 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.1 | 4640 | 41.6 | 3334.5 | -480 | 721.75 | 1201.75 | 10.45 | 85.4422 | 657 | 0 | 124.75 | 60 |  | 13.9091 | 1201.75
6 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83 | 4400 | 41.6 | 3334.5 | -240 | 732 | 972 | 10.8 | 82.8749 | 658 | 0 | 134 | 60 |  | 11.25 | 972
7 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 54 | 2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.05 | 4520 | 41.5 | 3217.5 | 120 | 1022.7 | 902.7 | 10.62 | 84.1769 | 978.2 | 0 | 44.5 | 0 |  | 10.4479 | 902.7
8 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 54 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 82.5 | 3300 | 41.5 | 3217.5 | -1220 | 1504.4574 | 958.5 | 10.65 | 85.0797 | 1430.8 | 1765.9574 | 133.6574 | 60 |  | 11.0938 | 958.5
9 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 35 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84 | 6800 | 41.21 | 2878.2 | 3500 | 5541.6531 | 909 | 10.1 | 86.5087 | 5579.84 | 1132.6531 | 21.8131 | 60 |  | 10.5208 | 909
10 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.15 | 4760 | 41.22 | 2889.9 | -2040 | 624.3191 | 909 | 10.1 | 88.2957 | 642.4 | 1755.3191 | 41.9191 | 60 |  | 10.5208 | 909
11 | 95 | 45 | 140 | 0 | 0 | 3 | 140 | 108 | 1.95 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.9 | 6560 | 41.65 | 3393 | 1800 | 3214 | 1414 | 10.1 | 86.7152 | 3204.7 | 0 | 69.3 | 60 |  | 16.3657 | 1414
12 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 54 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.25 | 7400 | 41.67 | 3416.4 | 840 | 4040.6667 | 909 | 10.1 | 85.9968 | 3981.2 | 2291.6667 | 119.4667 | 60 |  | 10.5208 | 909
13 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 83.95 | 6680 | 41.68 | 3428.1 | -720 | 3535.1995 | 949.5 | 10.55 | 82.9175 | 3650 | 3305.6995 | 5.1995 | 120 |  | 10.9896 | 949.5
14 | 60 | 145 | 205 | 0 | 0 | 3 | 205 | 80 | 1.3 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 83.45 | 5480 | 41.95 | 3744 | -1200 | 962.75 | 2162.75 | 10.55 | 83.9177 | 963.6 | 0 | 59.15 | 60 |  | 25.0318 | 2162.75
15 | 105 | 55 | 160 | 0 | 0 | 4 | 160 | 105 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83 | 4400 | 41.93 | 3720.6 | -1080 | 592 | 1672 | 10.45 | 85.6506 | 616 | 0 | 36 | 60 |  | 19.3519 | 1672
16 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 54 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83 | 4400 | 41.93 | 3720.6 | 0 | 4533.9043 | 1060.5 | 10.1 | 88.6187 | 4401.9 | 3473.4043 | 162.0043 | 30 |  | 12.2743 | 1060.5
17 | 120 | 40 | 160 | 0 | 0 | 3 | 160 | 80 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 83.15 | 4760 | 41.9 | 3685.5 | 360 | 1976 | 1616 | 10.1 | 88.2957 | 1952.5 | 0 | 83.5 | 60 |  | 18.7037 | 1616
18 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 50 | 0 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.4 | 5360 | 41.79 | 3556.8 | 600 | 1711 | 1111 | 10.1 | 87.7625 | 1677.9 | 0 | 93.1 | 60 |  | 12.8588 | 1111
19 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 50 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.35 | 5240 | 41.71 | 3463.2 | -120 | 3034.1989 | 858.5 | 10.1 | 87.8686 | 2919 | 2295.6989 | 175.1989 | 60 |  | 9.9363 | 858.5
20 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 55 | 0 | 2.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.3 | 5120 | 41.77 | 3533.4 | -120 | 2634.6809 | 1010 | 10.1 | 87.975 | 2471 | 1744.6809 | 223.6809 | 60 |  | 11.6898 | 1010
21 | 75 | 60 | 135 | 0 | 0 | 2 | 135 | 70 | 1.95 | 1.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83 | 4400 | 41.48 | 3194.1 | -720 | 2413.75 | 1383.75 | 10.25 | 87.3218 | 2456.6 | 1750 | 17.15 | 60 |  | 16.0156 | 1383.75
22 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 45 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 82.95 | 4290 | 41.43 | 3135.6 | -110 | 2509.1383 | 858.5 | 10.1 | 88.7269 | 2422 | 1760.6383 | 147.1383 | 60 |  | 9.9363 | 858.5
23 | 115 | 40 | 155 | 0 | 0 | 3 | 155 | 80 | 3 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 82.65 | 3630 | 41.93 | 3720.6 | -660 | 2762.0266 | 1650.75 | 10.65 | 84.7657 | 2868.9 | 1771.2766 | 13.1266 | 120 |  | 19.1059 | 1650.75
24 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83 | 4400 | 41.86 | 3638.7 | 770 | 3504.2766 | 963 | 10.7 | 83.6494 | 3615.325 | 1771.2766 | 8.9516 | 120 |  | 11.1458 | 963
25 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.05 | 4520 | 41.75 | 3510 | 120 | 2712.6735 | 909 | 10.1 | 88.5108 | 2521.05 | 1683.6735 | 191.6235 | 0 |  | 10.5208 | 909
26 | 95 | 95 | 190 | 0 | 0 | 3 | 190 | 100 | 2 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 82.5 | 3300 | 41.95 | 3744 | -1220 | 3037.6243 | 1919 | 10.1 | 89.7127 | 3038.75 | 2338.6243 | 58.8743 | 60 |  | 22.2106 | 1919
27 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 82.75 | 3850 | 41.68 | 3428.1 | 550 | 1560 | 1010 | 10.1 | 89.1624 | 1542.15 | 0 | 17.85 | 0 |  | 11.6898 | 1010
28 | 70 | 95 | 165 | 0 | 0 | 3 | 165 | 108 | 1.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 82.3 | 2860 | 41.66 | 3404.7 | -990 | 1936.0484 | 1732.5 | 10.5 | 86.7234 | 1792 | 1193.5484 | 204.0484 | 60 |  | 20.0521 | 1732.5
29 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 82.3 | 2860 | 41.48 | 3194.1 | 0 | 798.75 | 798.75 | 10.65 | 85.5019 | 664.3 | 0 | 134.45 | 0 |  | 9.2448 | 798.75
30 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 82.2 | 2640 | 41.52 | 3240.9 | -220 | 739.5 | 959.5 | 10.1 | 90.3822 | 664.3 | 0 | 135.2 | 60 |  | 11.1053 | 959.5
| 1800 | 1530 | 3330 | 0 | 0 | 98 | 3232 | 108 | 41.9 | 34.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 |  |  | 83.095 | 4657.3333 | 41.6333 | 3373.5 | -660 | 63786.3175 | 34412.2 | 10.334 | 86.4119 | 62442.615 | 30034.1175 | 2913.7025 | 1570 |  | 13.2763 | 34412.2