## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 40 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 82.15 | 2530 | 41.35 | 3042 | -110 | 698 | 808 | 10.1 | 90.4948 | 671.6 | 0 | 86.4 | 60 |  | 9.3519 | 808
2 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 55 | 0 | 2.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 82 | 2200 | 41.35 | 3042 | -330 | 672.25 | 1002.25 | 10.55 | 86.9597 | 644 | 0 | 88.25 | 60 |  | 11.6001 | 1002.25
3 | 80 | 0 | 80 | 0 | 0 | 6 | 80 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 81.95 | 2090 | 41.26 | 2936.7 | -110 | 750 | 860 | 10.75 | 85.4487 | 664.3 | 0 | 85.7 | 0 |  | 9.9537 | 860
4 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 40 | 0 | 1.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 81.8 | 1760 | 41.25 | 2925 | -330 | 637.5 | 967.5 | 10.75 | 85.7707 | 609 | 0 | 88.5 | 60 |  | 11.1979 | 967.5
5 | 75 | 0 | 75 | 0 | 0 | 6 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 81.8 | 1760 | 41.1 | 2749.5 | 0 | 798.75 | 798.75 | 10.65 | 86.5761 | 678.9 | 0 | 119.85 | 0 |  | 9.2448 | 798.75
6 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 40 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 81.75 | 1650 | 41 | 2632.5 | -110 | 746 | 856 | 10.7 | 86.2799 | 658 | 0 | 148 | 60 |  | 9.9074 | 856
7 | 120 | 0 | 120 | 0 | 0 | 6 | 120 | 54 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82.4 | 3080 | 41.26 | 2936.7 | 1430 | 2642 | 1212 | 10.1 | 89.9348 | 2520 | 0 | 182 | 60 |  | 14.0278 | 1212
8 | 0 | 150 | 150 | 0 | 0 | 6 | 150 | 54 | 0 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 82 | 2200 | 41.63 | 3369.6 | -880 | 702.5 | 1582.5 | 10.55 | 86.9597 | 642.4 | 0 | 60.1 | 0 |  | 18.316 | 1582.5
9 | 255 | 0 | 255 | 0 | 0 | 6 | 255 | 50 | 5.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 9 | 82.05 | 2310 | 41.7 | 3451.5 | 110 | 2749.25 | 2639.25 | 10.35 | 88.5294 | 2645.2 | 0 | 164.05 | 60 |  | 30.5469 | 2639.25
10 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 81.9 | 1980 | 41.45 | 3159 | -330 | 476.25 | 806.25 | 10.75 | 85.5557 | 476 | 0 | 60.25 | 60 |  | 9.3316 | 806.25
11 | 400 | 265 | 665 | 0 | 0 | 6 | 665 | 108 | 8.5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.1 | 7040 | 41.9 | 3685.5 | 5060 | 12845.6489 | 6716.5 | 10.1 | 86.3032 | 12814.8 | 1069.1489 | 90.8489 | 60 |  | 77.7373 | 6716.5
12 | 0 | 215 | 215 | 0 | 0 | 5 | 215 | 50 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.3 | 5120 | 41.53 | 3252.6 | -1920 | 4310.0106 | 2171.5 | 10.1 | 87.975 | 4235 | 4058.5106 | 175.0106 | 100 |  | 25.1331 | 2171.5
13 | 390 | 0 | 390 | 0 | 0 | 5 | 390 | 54 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 0 | ΒΛΑΒΗ ΜΕ ΤΟ ΟΡΙΟ ΦΟΡΤΙΟΥ & ΟΡΙΟ ΙΣΧΥΟΣ | 13 | 84.3 | 7520 | 41.38 | 3077.1 | 2400 | 8679.4255 | 3939 | 10.1 | 85.8952 | 8615.1 | 2340.4255 | 124.3255 | 60 |  | 45.5903 | 3939
14 | 730 | 560 | 1290 | 0 | 0 | 7 | 1290 | 110 | 15.65 | 12.47 | 0 | 0 | 0.8 | 0 | 0 | 0 | 11.5 | 0 | 1 | 1 | ΒΛ. ΜΕ ΤΟ ΟΡΙΟ Φ. & Ι. NoII - ΒΛ. ΡΥΘΜ. ΣΤΡ. ΝοΙ | 14 | 84.25 | 7400 | 41.9 | 3685.5 | -120 | 12909 | 13029 | 10.1 | 85.9968 | 12884.5 | 0 | 84.5 | 60 |  | 150.7986 | 13029
15 | 290 | 225 | 515 | 0 | 0 | 6 | 515 | 108 | 5.9 | 4.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 85.05 | 9320 | 41.78 | 3545.1 | 1920 | 9861.8782 | 5150 | 10 | 85.2427 | 9616.32 | 2791.8782 | 245.5582 | 0 |  | 59.6065 | 5150
16 | 105 | 530 | 635 | 0 | 0 | 5 | 635 | 80 | 2.7 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.5 | 8000 | 41.7 | 3451.5 | -1320 | 5093.5 | 6413.5 | 10.1 | 85.491 | 4971.3 | 0 | 182.2 | 60 |  | 74.2303 | 6413.5
17 | 85 | 0 | 85 | 0 | 0 | 5 | 85 | 42 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.5 | 8000 | 41.48 | 3194.1 | 0 | 858.5 | 858.5 | 10.1 | 85.491 | 678.9 | 0 | 239.6 | 60 |  | 9.9363 | 858.5
18 | 0 | 90 | 90 | 0 | 0 | 6 | 90 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560 | 41.5 | 3217.5 | -1440 | 1200.5851 | 922.5 | 10.25 | 85.4462 | 1035 | 1718.0851 | 165.5851 | 0 |  | 10.6771 | 922.5
19 | 105 | 0 | 105 | 0 | 0 | 6 | 105 | 40 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 41.63 | 3369.6 | -240 | 3102.4149 | 1060.5 | 10.1 | 86.9226 | 2933 | 2281.9149 | 229.4149 | 60 |  | 12.2743 | 1060.5
20 | 250 | 265 | 515 | 0 | 0 | 6 | 515 | 80 | 5.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 85.25 | 9800 | 41.75 | 3510 | 3480 | 10712.1122 | 5201.5 | 10.1 | 84.0085 | 10554.6 | 2030.6122 | 157.5122 | 0 |  | 60.2025 | 5201.5
21 | 540 | 400 | 940 | 0 | 0 | 5 | 940 | 108 | 12.78 | 9.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85 | 9200 | 41.77 | 3533.4 | -600 | 11761.0213 | 9494 | 10.1 | 84.4969 | 11636.2 | 2867.0213 | 184.8213 | 60 |  | 109.8843 | 9494
22 | 420 | 500 | 920 | 0 | 0 | 6 | 920 | 90 | 9.49 | 11.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 83.5 | 5600 | 41.6 | 3334.5 | -3600 | 8053.7021 | 9292 | 10.1 | 87.551 | 7971.6 | 2361.7021 | 142.1021 | 60 |  | 107.5463 | 9292
23 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.8 | 6320 | 41.46 | 3170.7 | 720 | 1511.25 | 791.25 | 10.55 | 83.215 | 1124.2 | 0 | 387.05 | 0 |  | 9.158 | 791.25
24 | 0 | 85 | 85 | 0 | 0 | 6 | 85 | 40 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.9 | 6560 | 41.43 | 3135.6 | 240 | 2161 | 858.5 | 10.1 | 86.7152 | 2044 | 1062.5 | 177 | 60 |  | 9.9363 | 858.5
25 | 70 | 0 | 70 | 0 | 0 | 5 | 70 | 35 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.8 | 6320 | 41.33 | 3018.6 | -240 | 2715.4583 | 731.5 | 10.45 | 84.0114 | 2620.7 | 2223.9583 | 94.7583 | 0 |  | 8.4664 | 731.5
26 | 0 | 90 | 90 | 0 | 0 | 6 | 90 | 50 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.85 | 6440 | 41.32 | 3006.9 | 120 | 2794.9574 | 909 | 10.1 | 86.8188 | 2591.5 | 1765.9574 | 203.4574 | 0 |  | 10.5208 | 909
27 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.1 | 7040 | 41.3 | 2983.5 | 600 | 6039.5789 | 808 | 10.1 | 86.3032 | 6041.95 | 4631.5789 | 57.6289 | 60 |  | 9.3519 | 808
28 | 0 | 95 | 95 | 0 | 0 | 6 | 95 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.9 | 6560 | 41.33 | 3018.6 | -480 | 7319.9255 | 959.5 | 10.1 | 86.7152 | 7236 | 6840.4255 | 143.9255 | 60 |  | 11.1053 | 959.5
29 | 390 | 45 | 435 | 0 | 0 | 6 | 435 | 95 | 9.05 | 0.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.2 | 7280 | 41.65 | 3393 | 720 | 6966.4574 | 4480.5 | 10.3 | 84.4269 | 6940.8 | 1765.9574 | 85.6574 | 60 |  | 51.8576 | 4480.5
30 | 0 | 605 | 605 | 0 | 0 | 6 | 605 | 54 | 0 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.3 | 9920 | 41.29 | 2971.8 | 2640 | 9290.3723 | 6352.5 | 10.5 | 80.7148 | 9241.8 | 297.8723 | 108.5723 | 60 |  | 73.5243 | 6352.5
31 | 705 | 90 | 795 | 0 | 0 | 0 | 795 | 108 | 13.65 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 83.3 | 5120 | 41.49 | 3205.8 | -4800 | 3793.6026 | 8029.5 | 10.1 | 87.975 | 3633 | 564.1026 | 220.6026 | 60 |  | 92.934 | 8029.5
| 5245 | 4550 | 9795 | 0 | 0 | 165 | 9630 | 110 | 115.5 | 102.45 | 0 | 0 | 0.8 | 0 | 0 | 0 | 20.5 | 0 | 28 | 24 |  |  | 83.4645 | 5580.6452 | 41.4797 | 3193.7226 | 2480 | 142852.9015 | 99701.25 | 10.1788 | 86.9476 | 139629.67 | 40671.6515 | 4583.2315 | 1360 |  | 37.2242 | 99701.25