## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 655 | 610 | 1265 | 0 | 0 | 10 | 1265 | 110 | 15 | 14.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 82.45 | 3190 | 41.58 | 3311.1 | -1930 | 11947.0946 | 13282.5 | 10.5 | 86.4018 | 11871.05 | 594.5946 | 136.0446 | 60 |  | 153.7326 | 13282.5
2 | 260 | 645 | 905 | 0 | 0 | 5 | 905 | 88 | 6.1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.4 | 5360 | 41.59 | 3322.8 | 2170 | 11672.5 | 9502.5 | 10.5 | 84.4191 | 11622.7 | 0 | 109.8 | 60 |  | 109.9826 | 9502.5
3 | 645 | 640 | 1285 | 0 | 0 | 5 | 1285 | 110 | 12.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 82.55 | 3410 | 41.82 | 3591.9 | -1950 | 12056.5 | 14006.5 | 10.9 | 83.0258 | 12078.99 | 0 | 37.51 | 60 |  | 162.1123 | 14006.5
4 | 100 | 645 | 745 | 0 | 0 | 5 | 745 | 110 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 83.85 | 6440 | 41.75 | 3510 | 3030 | 10778 | 7748 | 10.4 | 84.3144 | 10661 | 0 | 117 | 0 |  | 89.6759 | 7748
5 | 655 | 635 | 1290 | 0 | 0 | 5 | 1290 | 110 | 12.3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 83.8 | 6320 | 41.75 | 3510 | -120 | 13296 | 13416 | 10.4 | 84.4153 | 13260 | 0 | 66 | 30 |  | 155.2778 | 13416
6 | 650 | 660 | 1310 | 0 | 0 | 6 | 1310 | 108 | 12.32 | 12.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.9 | 8960 | 41.95 | 3744 | 2640 | 15609 | 12969 | 9.9 | 86.4048 | 15429 | 0 | 180 | 0 |  | 150.1042 | 12969
7 | 715 | 675 | 1390 | 0 | 0 | 4 | 1390 | 110 | 13.68 | 12.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 83.05 | 4520 | 41.82 | 3591.9 | -4440 | 11925.0535 | 14595 | 10.5 | 85.1389 | 11739 | 1770.0535 | 186.0535 | 0 |  | 168.9236 | 14595
8 | 625 | 620 | 1245 | 0 | 0 | 5 | 1245 | 108 | 12.26 | 11.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 82.6 | 3520 | 42 | 3802.5 | -1000 | 12570.5 | 13570.5 | 10.9 | 82.9236 | 12656 | 0 | 64.5 | 150 |  | 157.066 | 13570.5
9 | 640 | 625 | 1265 | 0 | 0 | 5 | 1265 | 108 | 12.11 | 12.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 83.7 | 6080 | 42 | 3802.5 | 2560 | 15969 | 13409 | 10.6 | 83.0211 | 16023 | 0 | 96 | 150 |  | 155.1968 | 13409
10 | 655 | 655 | 1310 | 0 | 0 | 4 | 1310 | 108 | 12.23 | 12.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 10 | 84.75 | 8600 | 42 | 3802.5 | 2520 | 15751 | 13231 | 10.1 | 84.991 | 15236.65 | 0 | 514.35 | 0 |  | 153.1366 | 13231
11 | 850 | 915 | 1765 | 0 | 0 | 5 | 1765 | 110 | 16.25 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.7 | 6080 | 41.87 | 3650.4 | -2520 | 15306.5 | 17826.5 | 10.1 | 87.1311 | 13986.3 | 0 | 138.2 | 60 |  | 206.3252 | 17826.5
12 | 110 | 775 | 885 | 0 | 0 | 4 | 885 | 110 | 2.05 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 83.4 | 5360 | 41.8 | 3568.5 | -720 | 8572.5 | 9292.5 | 10.5 | 84.4191 | 7955.7 | 0 | 676.8 | 60 |  | 107.5521 | 9292.5
13 | 260 | 110 | 370 | 0 | 0 | 5 | 370 | 55 | 5.77 | 2.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 85.3 | 9920 | 41.3 | 2983.5 | 4560 | 8223 | 3663 | 9.9 | 85.6066 | 7760.3 | 0 | 462.7 | 0 |  | 42.3958 | 3663
14 | 805 | 160 | 965 | 0 | 0 | 5 | 965 | 110 | 14.48 | 2.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.5 | 5600 | 41.75 | 3510 | -4320 | 5426.5 | 9746.5 | 10.1 | 87.551 | 5393.25 | 0 | 93.25 | 60 |  | 112.8067 | 9746.5
15 | 540 | 425 | 965 | 0 | 0 | 5 | 965 | 108 | 10.35 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 82.4 | 3080 | 41.78 | 3545.1 | -2520 | 7805.5 | 10325.5 | 10.7 | 84.8917 | 7809 | 0 | 56.5 | 60 |  | 119.5081 | 10325.5
16 | 165 | 695 | 860 | 0 | 0 | 4 | 860 | 109 | 2.97 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 82.7 | 3740 | 41.72 | 3474.9 | 660 | 9819 | 9159 | 10.65 | 84.6616 | 9842 | 0 | 37 | 60 |  | 106.0069 | 9159
17 | 360 | 0 | 360 | 0 | 0 | 5 | 360 | 54 | 6.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.85 | 8840 | 41.6 | 3334.5 | 5100 | 8700 | 3600 | 10 | 85.6406 | 8523.27 | 0 | 176.73 | 0 |  | 41.6667 | 3600
18 | 225 | 440 | 665 | 0 | 0 | 4 | 665 | 108 | 4.55 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.45 | 7880 | 40.99 | 2620.8 | -960 | 5756.5 | 6716.5 | 10.1 | 85.5917 | 5672.1 | 0 | 144.4 | 60 |  | 77.7373 | 6716.5
19 | 235 | 220 | 455 | 0 | 0 | 5 | 455 | 108 | 5.1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84.65 | 8360 | 40.96 | 2585.7 | 480 | 7964.9737 | 4595.5 | 10.1 | 85.1903 | 7825.6 | 2889.4737 | 139.3737 | 0 |  | 53.1887 | 4595.5
20 | 270 | 380 | 650 | 0 | 0 | 5 | 650 | 108 | 4.95 | 6.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.2 | 7280 | 41.04 | 2679.3 | -1080 | 7177.3077 | 6565 | 10.1 | 86.0987 | 7159.45 | 1692.3077 | 77.8577 | 60 |  | 75.9838 | 6565
21 | 305 | 275 | 580 | 0 | 0 | 4 | 580 | 108 | 6.15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.75 | 8600 | 41.84 | 3615.3 | 1320 | 9446.0412 | 5858 | 10.1 | 84.991 | 9380.5 | 2268.0412 | 125.5412 | 60 |  | 67.8009 | 5858
22 | 220 | 385 | 605 | 0 | 0 | 5 | 605 | 110 | 4 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.15 | 7160 | 41.9 | 3685.5 | -1440 | 4670.5 | 6110.5 | 10.1 | 86.2009 | 4533.3 | 0 | 197.2 | 60 |  | 70.7234 | 6110.5
23 | 265 | 245 | 510 | 0 | 0 | 5 | 510 | 110 | 5 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.2 | 7280 | 41.85 | 3627 | 120 | 5271 | 5151 | 10.1 | 86.0987 | 5283.6 | 0 | 47.4 | 60 |  | 59.6181 | 5151
24 | 275 | 295 | 570 | 0 | 0 | 4 | 570 | 110 | 6 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 85.05 | 9320 | 41.8 | 3568.5 | 2040 | 7740 | 5700 | 10 | 85.2427 | 7584.8 | 0 | 155.2 | 0 |  | 65.9722 | 5700
25 | 680 | 625 | 1305 | 0 | 0 | 5 | 1305 | 108 | 13.5 | 12.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.15 | 4760 | 41.75 | 3510 | -4560 | 10147.837 | 13506.75 | 10.35 | 86.1629 | 10042.1 | 1201.087 | 165.737 | 60 |  | 156.3281 | 13506.75
26 | 155 | 420 | 575 | 0 | 0 | 5 | 575 | 109 | 3 | 8.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 82.9 | 4180 | 41.83 | 3603.6 | -580 | 5457.5 | 6037.5 | 10.5 | 85.4512 | 5459.45 | 0 | 58.05 | 60 |  | 69.8785 | 6037.5
27 | 315 | 245 | 560 | 0 | 0 | 5 | 560 | 108 | 6.4 | 4.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84 | 6800 | 41.58 | 3311.1 | 2620 | 9446.2128 | 5656 | 10.1 | 86.5087 | 9298.72 | 1170.2128 | 207.4928 | 60 |  | 65.463 | 5656
28 | 145 | 365 | 510 | 0 | 0 | 4 | 510 | 108 | 2.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 83.6 | 5840 | 41.83 | 3603.6 | -960 | 5153.766 | 5151 | 10.1 | 87.3405 | 5112 | 962.766 | 101.766 | 60 |  | 59.6181 | 5151
29 | 200 | 210 | 410 | 0 | 0 | 5 | 410 | 108 | 4.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.15 | 4760 | 41.85 | 3627 | -1080 | 5468.2105 | 4264 | 10.4 | 85.7487 | 5495 | 2284.2105 | 33.2105 | 60 |  | 49.3519 | 4264
30 | 160 | 265 | 425 | 0 | 0 | 5 | 425 | 108 | 3.05 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 82.85 | 4070 | 41.8 | 3568.5 | -690 | 5395.9783 | 4292.5 | 10.1 | 88.9441 | 5413.56 | 1793.4783 | 42.4183 | 60 |  | 49.6817 | 4292.5
31 | 255 | 185 | 440 | 0 | 0 | 4 | 440 | 108 | 5.15 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 82.65 | 3630 | 41.91 | 3697.2 | -440 | 5759.3191 | 4444 | 10.1 | 89.3817 | 5779.02 | 1755.3191 | 40.2991 | 60 |  | 51.4352 | 4444
| 12395 | 14045 | 26440 | 0 | 0 | 152 | 26288 | 110 | 242.7 | 274.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 41 |  |  | 83.6984 | 6094.8387 | 41.71 | 3463.2 | -1490 | 290282.7943 | 273391.25 | 10.3401 | 85.1115 | 285886.41 | 18381.5443 | 5926.3843 | 1530 |  | 102.0726 | 273391.25