## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 330 | 150 | 480 | 0 | 0 | 5 | 480 | 110 | 6.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 82.6 | 3520 | 42.05 | 3861 | -110 | 6500.1622 | 4848 | 10.1 | 89.4918 | 6513.6 | 1762.1622 | 46.5622 | 60 |  | 56.1111 | 4848
2 | 100 | 240 | 340 | 0 | 0 | 4 | 340 | 110 | 2.7 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.45 | 7880 | 41.85 | 3627 | 4360 | 9512.0851 | 3434 | 10.1 | 85.5917 | 9396 | 1718.0851 | 176.0851 | 60 |  | 39.7454 | 3434
3 | 265 | 215 | 480 | 0 | 0 | 5 | 480 | 110 | 5 | 4.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 85 | 9200 | 41.93 | 3720.6 | 1320 | 8569.0417 | 4848 | 10.1 | 84.4969 | 8387.7 | 2401.0417 | 181.3417 | 0 |  | 56.1111 | 4848
4 | 300 | 325 | 625 | 0 | 0 | 4 | 625 | 110 | 6.08 | 5.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.3 | 7520 | 41.92 | 3708.9 | -1680 | 5254.0997 | 6281.25 | 10.05 | 86.3225 | 5112.38 | 652.8497 | 141.7197 | 0 |  | 72.6997 | 6281.25
5 | 275 | 110 | 385 | 0 | 0 | 5 | 385 | 98 | 6.02 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.75 | 6200 | 41.74 | 3498.3 | -1320 | 4908.9255 | 3888.5 | 10.1 | 87.0267 | 4898.04 | 2340.4255 | 70.8855 | 60 |  | 45.0058 | 3888.5
6 | 180 | 145 | 325 | 0 | 0 | 5 | 325 | 88 | 4.1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.55 | 5720 | 41.8 | 3568.5 | -480 | 2802.5 | 3282.5 | 10.1 | 87.4456 | 2817.8 | 0 | 44.7 | 60 |  | 37.9919 | 3282.5
7 | 165 | 100 | 265 | 0 | 0 | 5 | 265 | 86 | 3.7 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 83.2 | 4880 | 41.69 | 3439.8 | -840 | 3591.8191 | 2676.5 | 10.1 | 88.1885 | 3540.5 | 1755.3191 | 111.3191 | 60 |  | 30.978 | 2676.5
8 | 0 | 200 | 200 | 0 | 0 | 5 | 200 | 54 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.05 | 4520 | 41.85 | 3627 | -360 | 4120.4255 | 2140 | 10.7 | 83.5475 | 4139.75 | 2340.4255 | 40.6755 | 60 |  | 24.7685 | 2140
9 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 54 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 82.9 | 4180 | 41.83 | 3603.6 | -340 | 3389.2691 | 1973.95 | 10.67 | 84.0897 | 3306.9 | 1755.3191 | 142.3691 | 60 |  | 22.8466 | 1973.95
10 | 0 | 190 | 190 | 0 | 0 | 5 | 190 | 50 | 0 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.4 | 5360 | 41.75 | 3510 | 1180 | 4269.2128 | 1919 | 10.1 | 87.7625 | 4292.4 | 1170.2128 | 36.8128 | 60 |  | 22.2106 | 1919
11 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 40 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.6 | 8240 | 41.74 | 3498.3 | 2880 | 5397.8446 | 808 | 10.1 | 85.2903 | 5238.52 | 1709.8446 | 159.3246 | 0 |  | 9.3519 | 808
12 | 0 | 115 | 115 | 0 | 0 | 5 | 115 | 45 | 0 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.4 | 10160 | 41.95 | 3744 | 1920 | 4220.6753 | 1161.5 | 10.1 | 83.7181 | 4160.05 | 1139.1753 | 60.6253 | 0 |  | 13.4433 | 1161.5
13 | 180 | 0 | 180 | 0 | 0 | 5 | 180 | 50 | 4.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 85.2 | 9680 | 41.87 | 3650.4 | -480 | 3678.4255 | 1818 | 10.1 | 84.1057 | 3642.7 | 2340.4255 | 95.7255 | 60 |  | 21.0417 | 1818
14 | 100 | 215 | 315 | 0 | 0 | 4 | 315 | 80 | 2.55 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.65 | 8360 | 41.81 | 3580.2 | -1320 | 4201.9255 | 3181.5 | 10.1 | 85.1903 | 4197.5 | 2340.4255 | 64.4255 | 60 |  | 36.8229 | 3181.5
15 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.6 | 8240 | 41.76 | 3521.7 | -120 | 3477.9894 | 656.5 | 10.1 | 85.2903 | 3493 | 2941.4894 | 44.9894 | 60 |  | 7.5984 | 656.5
16 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.5 | 8000 | 41.37 | 3065.4 | -240 | 2227.6383 | 707 | 10.1 | 85.491 | 2197.3 | 1760.6383 | 90.3383 | 60 |  | 8.1829 | 707
17 | 0 | 110 | 110 | 0 | 0 | 5 | 110 | 54 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 84.55 | 8120 | 41.5 | 3217.5 | 120 | 1209 | 1089 | 9.9 | 87.1156 | 1011.7 | 0 | 197.3 | 0 |  | 12.6042 | 1089
18 | 40 | 95 | 135 | 0 | 0 | 5 | 135 | 80 | 1 | 2.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 83.95 | 6680 | 41.65 | 3393 | -1440 | 2646.9043 | 1363.5 | 10.1 | 86.6118 | 2550.45 | 2723.4043 | 96.4543 | 0 |  | 15.7812 | 1363.5
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.45 | 5480 | 41.56 | 3287.7 | -1200 | 2469.766 | 707 | 10.1 | 87.6566 | 2469.6 | 2962.766 | 60.166 | 60 |  | 8.1829 | 707
20 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 40 | 0 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.05 | 4520 | 41.53 | 3252.6 | -960 | 2560.6579 | 757.5 | 10.1 | 88.5108 | 2426.4 | 2763.1579 | 134.2579 | 0 |  | 8.7674 | 757.5
21 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 82.95 | 4290 | 41.5 | 3217.5 | -230 | 515.5 | 745.5 | 10.65 | 84.1448 | 574 | 0 | 21.5 | 80 |  | 8.6285 | 745.5
22 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.85 | 6440 | 41.34 | 3030.3 | 2150 | 4540.6735 | 707 | 10.1 | 86.8188 | 4456.8 | 1683.6735 | 83.8735 | 0 |  | 8.1829 | 707
23 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.7 | 6080 | 41.18 | 2843.1 | -360 | 3550.2706 | 776.25 | 10.35 | 85.0265 | 3540.5 | 3134.0206 | 69.7706 | 60 |  | 8.9844 | 776.25
24 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 36 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.3 | 5120 | 41.34 | 3030.3 | -960 | 3106.0106 | 757.5 | 10.1 | 87.975 | 2807 | 3308.5106 | 299.0106 | 0 |  | 8.7674 | 757.5
25 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 49 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.6 | 5840 | 41.51 | 3229.2 | 720 | 3459.0699 | 959.5 | 10.1 | 87.3405 | 3450 | 1779.5699 | 69.0699 | 60 |  | 11.1053 | 959.5
26 | 0 | 120 | 120 | 0 | 0 | 5 | 120 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.5 | 5600 | 41.55 | 3276 | -240 | 960 | 1200 | 10 | 88.4265 | 720.3 | 0 | 239.7 | 0 |  | 13.8889 | 1200
27 | 15 | 0 | 15 | 0 | 0 | 3 | 15 | 15 | 0.15 | 0 | 0 | 0 | 0 | 5.67 | 0 | 0 | 0 | 5.67 | 1 | 0 | ΒΛΑΒΗ Κ.Γ. ΔΕΔΔΗΕ 20KV | 27 | 83.5 | 5600 | 41.1 | 2749.5 | 0 | 1188.3421 | 151.5 | 10.1 | 87.551 | 644 | 1036.8421 | 544.3421 | 0 |  | 1.7535 | 151.5
28 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 5.4 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 7.5 | 0 | 3 | ΒΛΑΒΗ Κ.Γ. ΔΕΔΔΗΕ 20KV | 28 | 83.45 | 5480 | 41.85 | 3627 | -120 | 4174.7766 | 2523.5 | 10.3 | 85.9545 | 4060 | 1771.2766 | 174.7766 | 60 |  | 29.2072 | 2523.5
| 2595 | 2860 | 5455 | 0 | 0 | 126 | 5329 | 110 | 58.3 | 63.55 | 0 | 0 | 0 | 13.17 | 0 | 0 | 0 | 13.17 | 21 | 23 |  |  | 83.8571 | 6461.0714 | 41.6614 | 3406.3714 | 1850 | 106503.0108 | 55361.95 | 10.1488 | 86.3862 | 104044.89 | 49291.0608 | 3498.1208 | 1040 |  | 22.8844