## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 355 | 265 | 620 | 0 | 0 | 4 | 620 | 80 | 8.78 | 7.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.25 | 5000 | 41.87 | 3650.4 | -480 | 5782 | 6262 | 10.1 | 88.0816 | 5778.25 | 0 | 63.75 | 60 |  | 72.4769 | 6262
2 | 0 | 210 | 210 | 0.5 | 0.0022 | 5 | 210 | 55 | 0 | 4.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.95 | 9080 | 41.79 | 3556.8 | 4080 | 6148.5 | 2068.5 | 9.85 | 86.7423 | 5722.9 | 0 | 425.6 | 0 |  | 23.941 | 2068.5
3 | 310 | 205 | 515 | 0 | 0 | 5 | 515 | 110 | 6.12 | 4.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.25 | 7400 | 41.56 | 3287.7 | -1680 | 3418.5 | 5098.5 | 9.9 | 87.7341 | 3281.85 | 0 | 136.65 | 0 |  | 59.0104 | 5098.5
4 | 35 | 560 | 595 | 0 | 0 | 5 | 595 | 100 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 83.35 | 5240 | 41.86 | 3638.7 | -2160 | 5037.672 | 6009.5 | 10.1 | 87.8686 | 4907 | 1188.172 | 190.672 | 60 |  | 69.5544 | 6009.5
5 | 340 | 280 | 620 | 0 | 0 | 4 | 620 | 108 | 7.75 | 18.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 83.65 | 5960 | 41.63 | 3369.6 | 720 | 6982 | 6262 | 10.1 | 87.2357 | 6921.2 | 0 | 120.8 | 60 |  | 72.4769 | 6262
6 | 95 | 490 | 585 | 0 | 0 | 5 | 585 | 70 | 2.6 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 6 | 82.3 | 2860 | 41.84 | 3615.3 | -3100 | 3101 | 6201 | 10.6 | 85.9052 | 2883.85 | 0 | 277.15 | 60 |  | 71.7708 | 6201
7 | 140 | 0 | 140 | 0 | 0 | 5 | 140 | 54 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82 | 2200 | 41.46 | 3170.7 | -660 | 817 | 1477 | 10.55 | 86.9597 | 672 | 0 | 205 | 60 |  | 17.0949 | 1477
8 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 55 | 0 | 2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.25 | 5000 | 41.26 | 2936.7 | 2800 | 3709 | 909 | 10.1 | 88.0816 | 3244.7 | 0 | 464.3 | 0 |  | 10.5208 | 909
9 | 305 | 455 | 760 | 0 | 0 | 5 | 760 | 105 | 8 | 10.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 83.75 | 6200 | 41.84 | 3615.3 | 1200 | 8876 | 7676 | 10.1 | 87.0267 | 8551.4 | 0 | 384.6 | 60 |  | 88.8426 | 7676
10 | 240 | 330 | 570 | 0 | 0 | 5 | 570 | 108 | 4.95 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 82 | 2200 | 41.6 | 3334.5 | -4000 | 2156 | 6156 | 10.8 | 84.9468 | 2159.7 | 0 | 56.3 | 60 |  | 71.25 | 6156
11 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 49 | 2.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 82.95 | 4290 | 41.22 | 2889.9 | 2090 | 3234.5 | 1144.5 | 10.9 | 82.2148 | 3158.4 | 0 | 76.1 | 0 |  | 13.2465 | 1144.5
12 | 55 | 315 | 370 | 0 | 0 | 5 | 370 | 75 | 1.47 | 6.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 82.85 | 4070 | 41.74 | 3498.3 | -220 | 5857.4255 | 3737 | 10.1 | 88.9441 | 5788.9 | 2340.4255 | 128.5255 | 60 |  | 43.2523 | 3737
13 | 270 | 55 | 325 | 0 | 0 | 4 | 325 | 55 | 6 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.55 | 8120 | 41.66 | 3404.7 | 4050 | 7332.5 | 3282.5 | 10.1 | 85.3905 | 7178 | 0 | 154.5 | 0 |  | 37.9919 | 3282.5
14 | 240 | 350 | 590 | 0 | 0 | 5 | 590 | 110 | 5.2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 14 | 83.65 | 5960 | 41.65 | 3393 | -2160 | 5564.9574 | 5959 | 10.1 | 87.2357 | 5599.1 | 1765.9574 | 25.8574 | 60 |  | 68.9699 | 5959
15 | 305 | 110 | 415 | 0 | 0 | 4 | 415 | 80 | 7.6 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83.9 | 6560 | 41.77 | 3533.4 | 600 | 4791.5 | 4191.5 | 10.1 | 86.7152 | 4526.2 | 0 | 265.3 | 0 |  | 48.5127 | 4191.5
16 | 170 | 275 | 445 | 0 | 0 | 4 | 445 | 100 | 4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.5 | 8000 | 41.81 | 3580.2 | 1440 | 5934.5 | 4494.5 | 10.1 | 85.491 | 5759.7 | 0 | 234.8 | 60 |  | 52.0197 | 4494.5
17 | 155 | 25 | 180 | 0 | 0 | 5 | 180 | 100 | 3.6 | 0.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85.15 | 9560 | 41.63 | 3369.6 | 1560 | 5104.8182 | 1863 | 10.35 | 82.1693 | 4832 | 1681.8182 | 272.8182 | 0 |  | 21.5625 | 1863
18 | 260 | 445 | 705 | 0 | 0 | 5 | 705 | 110 | 6.1 | 10.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.05 | 6920 | 41.86 | 3638.7 | -2640 | 7356.7756 | 7155.75 | 10.15 | 85.9802 | 7377.8 | 2841.0256 | 38.9756 | 60 |  | 82.8212 | 7155.75
19 | 220 | 0 | 220 | 0 | 0 | 5 | 220 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.95 | 9080 | 41.79 | 3556.8 | 2160 | 6075.8776 | 2222 | 10.1 | 84.5953 | 5943.2 | 1693.8776 | 132.6776 | 0 |  | 25.7176 | 2222
20 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.15 | 9560 | 40.94 | 2562.3 | 480 | 2886.7172 | 735 | 9.8 | 86.7808 | 2776.8 | 1671.7172 | 109.9172 | 0 |  | 8.5069 | 735
21 | 100 | 0 | 100 | 0 | 0 | 6 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.05 | 9320 | 41.05 | 2691 | -240 | 3026.4103 | 1010 | 10.1 | 84.3988 | 2977.5 | 2256.4103 | 108.9103 | 60 |  | 11.6898 | 1010
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 40 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.15 | 9560 | 41.04 | 2679.3 | 240 | 5623.9162 | 808 | 10.1 | 84.2032 | 5350.9 | 4575.9162 | 273.0162 | 0 |  | 9.3519 | 808
23 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 40 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.55 | 8120 | 41.34 | 3030.3 | -1440 | 4166.4153 | 1262.5 | 10.1 | 85.3905 | 4119.85 | 4343.9153 | 106.5653 | 60 |  | 14.6123 | 1262.5
24 | 40 | 145 | 185 | 0 | 0 | 4 | 185 | 94 | 0.65 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.1 | 7040 | 41.87 | 3650.4 | -1080 | 3640.4663 | 1850 | 10 | 87.1663 | 3291.8 | 2870.4663 | 348.6663 | 0 |  | 21.412 | 1850
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.75 | 8600 | 41.34 | 3030.3 | 1560 | 4831.1026 | 707 | 10.1 | 84.991 | 4824.45 | 2564.1026 | 16.6526 | 10 |  | 8.1829 | 707
26 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.4 | 7760 | 41.27 | 2948.4 | -840 | 3845.7234 | 707 | 10.1 | 85.6926 | 3686.5 | 3978.7234 | 179.2234 | 20 |  | 8.1829 | 707
27 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.6 | 8240 | 41.21 | 2878.2 | 480 | 3440.8071 | 707 | 10.1 | 85.2903 | 3419.55 | 2253.8071 | 81.2571 | 60 |  | 8.1829 | 707
28 | 60 | 155 | 215 | 0 | 0 | 4 | 215 | 100 | 1.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 85 | 9200 | 41.83 | 3603.6 | 960 | 5963.1327 | 2171.5 | 10.1 | 84.4969 | 5872.5 | 2831.6327 | 90.6327 | 0 |  | 25.1331 | 2171.5
29 | 220 | 140 | 360 | 0 | 0 | 5 | 360 | 55 | 5.3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.4 | 7760 | 42.07 | 3884.4 | -1440 | 4467.7949 | 3636 | 10.1 | 85.6926 | 4294 | 2271.7949 | 233.7949 | 60 |  | 42.0833 | 3636
30 | 175 | 380 | 555 | 0 | 0 | 4 | 555 | 110 | 3.6 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 30 | 84.25 | 7400 | 41.84 | 3615.3 | -360 | 7901.75 | 5605.5 | 10.1 | 85.9968 | 7829.95 | 2656.25 | 131.8 | 60 |  | 64.8785 | 5605.5
31 | 100 | 45 | 145 | 0 | 0 | 4 | 145 | 90 | 2.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.05 | 6920 | 41.81 | 3580.2 | -480 | 984.5 | 1464.5 | 10.1 | 86.4059 | 722.7 | 0 | 321.8 | 60 |  | 16.9502 | 1464.5
| 4560 | 5550 | 10110 | 0.5 | 0.0022 | 142 | 9967.4978 | 110 | 105.3 | 125.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32 |  |  | 84.0242 | 6876.7742 | 41.5952 | 3328.8387 | 1440 | 148059.2623 | 102833.25 | 10.1714 | 85.8517 | 143452.65 | 43786.0123 | 5656.6123 | 1050 |  | 38.3935 | 102833.25