## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 490 | 580 | 1070 | 0 | 0 | 3 | 1070 | 108 | 11.49 | 13.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 1 | 85.15 | 9560 | 41.95 | 3744 | 1440 | 12247 | 10807 | 10.1 | 84.2032 | 12130.83 | 0 | 176.17 | 60 |  | 125.081 | 10807
2 | 165 | 620 | 785 | 0 | 0 | 3 | 785 | 108 | 4.21 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.95 | 9080 | 42 | 3802.5 | -480 | 9186.7199 | 7928.5 | 10.1 | 84.5953 | 8932.5 | 1738.2199 | 314.2199 | 60 |  | 91.765 | 7928.5
3 | 365 | 330 | 695 | 0 | 0 | 3 | 695 | 100 | 7.51 | 6.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 83.75 | 6200 | 41.98 | 3779.1 | -2880 | 7192.1316 | 7019.5 | 10.1 | 87.0267 | 7234.71 | 3052.6316 | 17.4216 | 60 |  | 81.2442 | 7019.5
4 | 325 | 365 | 690 | 0 | 0 | 3 | 690 | 108 | 7.05 | 7.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 83.9 | 6560 | 42.08 | 3896.1 | 360 | 7329 | 6969 | 10.1 | 86.7152 | 7341.96 | 0 | 47.04 | 60 |  | 80.6597 | 6969
5 | 410 | 305 | 715 | 0 | 0 | 3 | 715 | 108 | 8.09 | 6.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.1 | 7040 | 41.92 | 3708.9 | 480 | 9426.8886 | 7221.5 | 10.1 | 86.3032 | 9435 | 1725.3886 | 51.8886 | 60 |  | 83.5822 | 7221.5
6 | 290 | 400 | 690 | 0 | 0 | 3 | 690 | 100 | 6.15 | 8.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.4 | 7760 | 42.02 | 3825.9 | 720 | 7620 | 6900 | 10 | 86.5495 | 7394.9 | 0 | 225.1 | 0 |  | 79.8611 | 6900
7 | 400 | 290 | 690 | 0 | 0 | 3 | 690 | 100 | 8.2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 84.65 | 8360 | 42 | 3802.5 | 600 | 7569 | 6969 | 10.1 | 85.1903 | 7219.7 | 0 | 349.3 | 0 |  | 80.6597 | 6969
8 | 405 | 400 | 805 | 0 | 0 | 3 | 805 | 100 | 8.2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 85.1 | 9440 | 41.79 | 3556.8 | 1080 | 9210.5 | 8130.5 | 10.1 | 84.3008 | 8584.8 | 0 | 625.7 | 0 |  | 94.103 | 8130.5
9 | 390 | 315 | 705 | 0 | 0 | 3 | 705 | 100 | 8.2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 85.25 | 9800 | 41.89 | 3673.8 | 360 | 7480.5 | 7120.5 | 10.1 | 84.0085 | 7288.4 | 0 | 252.1 | 60 |  | 82.4132 | 7120.5
10 | 220 | 310 | 530 | 0 | 0 | 3 | 530 | 100 | 4.6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.35 | 7640 | 41.98 | 3779.1 | -2160 | 10588.8333 | 5353 | 10.1 | 85.7938 | 10585 | 7395.8333 | 63.8333 | 60 |  | 61.956 | 5353
11 | 415 | 420 | 835 | 0 | 0 | 3 | 835 | 108 | 8.2 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.95 | 9080 | 42.08 | 3896.1 | 1440 | 9873.5 | 8433.5 | 10.1 | 84.5953 | 9636.8 | 0 | 236.7 | 0 |  | 97.61 | 8433.5
12 | 145 | 360 | 505 | 0 | 0 | 3 | 505 | 100 | 2.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85 | 9200 | 42.11 | 3931.2 | 120 | 5220.5 | 5100.5 | 10.1 | 84.4969 | 4876.4 | 0 | 344.1 | 0 |  | 59.0336 | 5100.5
13 | 315 | 105 | 420 | 0 | 0 | 3 | 420 | 110 | 6.5 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.5 | 8000 | 41.6 | 3334.5 | -1200 | 5403.7021 | 4242 | 10.1 | 85.491 | 5365.5 | 2361.7021 | 98.2021 | 60 |  | 49.0972 | 4242
14 | 0 | 445 | 445 | 0 | 0 | 3 | 445 | 54 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.5 | 8000 | 41.52 | 3240.9 | 0 | 5029.7872 | 4450 | 10 | 86.3459 | 4620 | 579.7872 | 409.7872 | 0 |  | 51.5046 | 4450
15 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.05 | 9320 | 41.31 | 2995.2 | 1320 | 8220.3128 | 4595.5 | 10.1 | 84.3988 | 7999.2 | 2304.8128 | 281.1128 | 60 |  | 53.1887 | 4595.5
16 | 230 | 390 | 620 | 0 | 0 | 2 | 620 | 110 | 4.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 16 | 84.4 | 7760 | 41.98 | 3779.1 | -1560 | 5851.7326 | 6262 | 10.1 | 85.6926 | 5738.4 | 1149.7326 | 173.3326 | 60 |  | 72.4769 | 6262
17 | 345 | 160 | 505 | 0 | 0 | 3 | 505 | 100 | 7.1 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7040 | 41.77 | 3533.4 | -720 | 5641.0745 | 5201.5 | 10.3 | 84.6274 | 5628.3 | 1159.5745 | 72.7745 | 60 |  | 60.2025 | 5201.5
18 | 395 | 90 | 485 | 0 | 0 | 3 | 485 | 100 | 7.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 18 | 85.3 | 9920 | 41.02 | 2655.9 | 2880 | 10730.6277 | 4898.5 | 10.1 | 83.9115 | 10752.9 | 2952.1277 | 37.7277 | 60 |  | 56.6956 | 4898.5
19 | 690 | 0 | 690 | 0 | 0 | 4 | 690 | 55 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 2 | 0 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 19 | 84.5 | 8000 | 41.34 | 3030.3 | -1920 | 8000.8717 | 6969 | 10.1 | 85.491 | 7948.8 | 2951.8717 | 112.0717 | 60 |  | 80.6597 | 6969
20 | 745 | 0 | 745 | 0 | 0 | 3 | 745 | 54 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 2 | 0 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 20 | 83.6 | 5840 | 42 | 3802.5 | -2160 | 7449.734 | 7822.5 | 10.5 | 84.0133 | 7458.9 | 1787.234 | 50.834 | 60 |  | 90.5382 | 7822.5
21 | 565 | 235 | 800 | 0 | 0 | 3 | 800 | 50 | 12.05 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.8 | 8720 | 41.98 | 3779.1 | 2880 | 12814.0426 | 8200 | 10.25 | 83.6494 | 12854.25 | 1734.0426 | 19.7926 | 60 |  | 94.9074 | 8200
22 | 590 | 765 | 1355 | 0 | 0 | 2 | 1355 | 110 | 11.35 | 15.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 22 | 85.25 | 9800 | 42 | 3802.5 | 1080 | 14765.5 | 13685.5 | 10.1 | 84.0085 | 14755.6 | 0 | 69.9 | 60 |  | 158.397 | 13685.5
23 | 720 | 495 | 1215 | 0 | 0 | 4 | 1215 | 110 | 14.5 | 9.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 23 | 83.8 | 6320 | 42 | 3802.5 | -3480 | 9156 | 12636 | 10.4 | 84.4153 | 9176.1 | 0 | 39.9 | 60 |  | 146.25 | 12636
24 | 240 | 625 | 865 | 0 | 0 | 3 | 865 | 108 | 4.3 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84 | 6800 | 42 | 3802.5 | 480 | 9216.5 | 8736.5 | 10.1 | 86.5087 | 9117.7 | 0 | 158.8 | 60 |  | 101.1169 | 8736.5
25 | 820 | 415 | 1235 | 0 | 0 | 3 | 1235 | 108 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 25 | 84.1 | 7040 | 41.95 | 3744 | 240 | 12812.3 | 12572.3 | 10.18 | 85.625 | 12859.2 | 0 | 13.1 | 60 |  | 145.5127 | 12572.3
26 | 250 | 710 | 960 | 0 | 0 | 3 | 960 | 108 | 3.75 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 26 | 84.3 | 7520 | 41.95 | 3744 | 480 | 10176 | 9696 | 10.1 | 85.8952 | 10015.6 | 0 | 190.4 | 30 |  | 112.2222 | 9696
27 | 575 | 170 | 745 | 0 | 0 | 3 | 745 | 110 | 28.82 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.35 | 7640 | 41.98 | 3779.1 | 120 | 7644.5 | 7524.5 | 10.1 | 85.7938 | 7509.6 | 0 | 164.9 | 30 |  | 87.0891 | 7524.5
28 | 155 | 795 | 950 | 0 | 0 | 4 | 950 | 110 | 3.1 | 14.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 28 | 85.1 | 9440 | 42 | 3802.5 | 1800 | 12559.8936 | 9595 | 10.1 | 84.3008 | 12488.9 | 1164.8936 | 130.9936 | 60 |  | 111.0532 | 9595
29 | 750 | 235 | 985 | 0 | 0 | 3 | 985 | 108 | 14.03 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 85.05 | 9320 | 42 | 3802.5 | -120 | 10859.5337 | 9850 | 10 | 85.2427 | 10599.6 | 1129.5337 | 259.9337 | 0 |  | 114.0046 | 9850
30 | 275 | 690 | 965 | 0 | 0 | 3 | 965 | 110 | 5.22 | 12.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.9 | 6560 | 41.94 | 3732.3 | -2760 | 8260.4194 | 9843 | 10.2 | 85.865 | 8246 | 1177.4194 | 74.4194 | 60 |  | 113.9236 | 9843
31 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 55 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.1 | 7040 | 41.93 | 3720.6 | 480 | 9284.0426 | 7070 | 10.1 | 86.3032 | 9093 | 1734.0426 | 191.0426 | 0 |  | 81.8287 | 7070
| 12835 | 11020 | 23855 | 0 | 0 | 94 | 23761 | 110 | 273.17 | 223.47 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 56 | 52 |  |  | 84.5242 | 8058.0645 | 41.8732 | 3654.1742 | -1080 | 276821.1478 | 241802.3 | 10.1363 | 85.136 | 272888.55 | 36098.8478 | 5252.5978 | 1320 |  | 90.2786 | 241802.3