## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 660 | 210 | 870 | 0 | 0 | 3 | 870 | 108 | 13.01 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 83.95 | 6680 | 42 | 3802.5 | -360 | 9616.1892 | 8787 | 10.1 | 86.6118 | 9473.7 | 1189.1892 | 202.4892 | 60 |  | 101.7014 | 8787
2 | 295 | 630 | 925 | 0 | 0 | 3 | 925 | 108 | 7.02 | 13.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.2 | 7280 | 42 | 3802.5 | 600 | 11316.6892 | 9527.5 | 10.3 | 84.4269 | 11277 | 1189.1892 | 99.6892 | 60 |  | 110.272 | 9527.5
3 | 635 | 165 | 800 | 0 | 0 | 3 | 800 | 90 | 12.51 | 3.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.35 | 7640 | 42 | 3802.5 | 360 | 8440 | 8080 | 10.1 | 85.7938 | 8358.5 | 0 | 141.5 | 60 |  | 93.5185 | 8080
4 | 0 | 700 | 700 | 0 | 0 | 3 | 700 | 55 | 0 | 13.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85 | 9200 | 41.8 | 3568.5 | 1560 | 9821.4894 | 7070 | 10.1 | 84.4969 | 9628.7 | 1191.4894 | 252.7894 | 60 |  | 81.8287 | 7070
5 | 675 | 160 | 835 | 0 | 0 | 3 | 835 | 108 | 13.1 | 3.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.3 | 7520 | 42 | 3802.5 | -1680 | 7923.7128 | 8433.5 | 10.1 | 85.8952 | 7944.9 | 1170.2128 | 38.8128 | 60 |  | 97.61 | 8433.5
6 | 0 | 670 | 670 | 0 | 0 | 3 | 670 | 54 | 0 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 83.9 | 6560 | 41.9 | 3685.5 | -960 | 7562.3191 | 6767 | 10.1 | 86.7152 | 7447.9 | 1755.3191 | 174.4191 | 60 |  | 78.3218 | 6767
7 | 635 | 0 | 635 | 0 | 0 | 3 | 635 | 54 | 13.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.65 | 5960 | 41.65 | 3393 | -600 | 8754.9894 | 6413.5 | 10.1 | 87.2357 | 8763.15 | 2941.4894 | 51.8394 | 60 |  | 74.2303 | 6413.5
8 | 95 | 630 | 725 | 0 | 0 | 3 | 725 | 75 | 2.65 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.5 | 8000 | 41.99 | 3790.8 | 2040 | 12421.3235 | 7322.5 | 10.1 | 85.491 | 12398.8 | 3058.8235 | 82.5235 | 60 |  | 84.7512 | 7322.5
9 | 325 | 575 | 900 | 0 | 0 | 3 | 900 | 90 | 7.93 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 83.95 | 6680 | 42.05 | 3861 | -1320 | 10241.7204 | 9180 | 10.2 | 85.7627 | 10290 | 2381.7204 | 11.7204 | 60 |  | 106.25 | 9180
10 | 65 | 615 | 680 | 0 | 0 | 3 | 680 | 85 | 1.63 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 41.86 | 3638.7 | -360 | 7799.1892 | 6970 | 10.25 | 85.6506 | 7770 | 1189.1892 | 89.1892 | 60 |  | 80.6713 | 6970
11 | 645 | 85 | 730 | 0 | 0 | 3 | 730 | 70 | 13.05 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.8 | 8720 | 41.97 | 3767.4 | 2400 | 12113.4255 | 7373 | 10.1 | 84.8917 | 11949.3 | 2340.4255 | 164.1255 | 0 |  | 85.3356 | 7373
12 | 170 | 595 | 765 | 0 | 0 | 3 | 765 | 90 | 4.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 12 | 84.2 | 7280 | 41.73 | 3486.6 | -1440 | 8648.2021 | 7726.5 | 10.1 | 86.0987 | 8562.6 | 2361.7021 | 145.6021 | 60 |  | 89.4271 | 7726.5
13 | 665 | 30 | 695 | 0 | 0 | 3 | 695 | 104 | 13.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.1 | 7040 | 42.02 | 3825.9 | -240 | 6779.5 | 7019.5 | 10.1 | 86.3032 | 6776 | 0 | 63.5 | 60 |  | 81.2442 | 7019.5
14 | 0 | 615 | 615 | 0 | 0 | 3 | 615 | 53 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.7 | 6080 | 42.07 | 3884.4 | -960 | 7001.5 | 6211.5 | 10.1 | 87.1311 | 6901.2 | 1750 | 160.3 | 60 |  | 71.8924 | 6211.5
15 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 55 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.15 | 7160 | 41.9 | 3685.5 | 1080 | 8853.3065 | 6047.5 | 10.25 | 84.9394 | 8827 | 1725.8065 | 86.3065 | 60 |  | 69.9942 | 6047.5
16 | 50 | 665 | 715 | 0 | 0 | 2 | 715 | 80 | 1.1 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.65 | 8360 | 41.91 | 3697.2 | 1200 | 8421.5 | 7221.5 | 10.1 | 85.1903 | 8088.4 | 0 | 393.1 | 60 |  | 83.5822 | 7221.5
17 | 530 | 110 | 640 | 0 | 0 | 3 | 640 | 80 | 10.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7040 | 42 | 3802.5 | -1320 | 8633.3617 | 6464 | 10.1 | 86.3032 | 8611.2 | 3489.3617 | 82.1617 | 60 |  | 74.8148 | 6464
18 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.8 | 6320 | 42.05 | 3861 | -720 | 7521.3441 | 5865 | 10.2 | 86.0705 | 7521 | 2376.3441 | 60.3441 | 60 |  | 67.8819 | 5865
19 | 565 | 370 | 935 | 0 | 0 | 3 | 935 | 100 | 11.6 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84 | 6800 | 42.05 | 3861 | 480 | 9923.5 | 9443.5 | 10.1 | 86.5087 | 9968.4 | 0 | 15.1 | 60 |  | 109.2998 | 9443.5
20 | 85 | 555 | 640 | 0 | 0 | 3 | 640 | 84 | 1.75 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 83.6 | 5840 | 42 | 3802.5 | -960 | 7264.3613 | 6579.2 | 10.28 | 85.8112 | 7235.2 | 1645.1613 | 89.1613 | 60 |  | 76.1481 | 6579.2
21 | 495 | 205 | 700 | 0 | 0 | 3 | 700 | 110 | 11.11 | 4.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 83.85 | 6440 | 42 | 3802.5 | 600 | 9444.1935 | 7070 | 10.1 | 86.8188 | 9345 | 1774.1935 | 159.1935 | 60 |  | 81.8287 | 7070
22 | 540 | 805 | 1345 | 0 | 0 | 3 | 1345 | 110 | 11.14 | 15.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 22 | 84.6 | 8240 | 42 | 3802.5 | 1800 | 15384.5 | 13584.5 | 10.1 | 85.2903 | 15273.6 | 0 | 110.9 | 0 |  | 157.228 | 13584.5
23 | 500 | 175 | 675 | 0 | 0 | 3 | 675 | 55 | 10 | 4.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.25 | 9800 | 42.06 | 3872.7 | 1560 | 8175 | 6615 | 9.8 | 86.5802 | 7950 | 0 | 225 | 0 |  | 76.5625 | 6615
24 | 155 | 505 | 660 | 0 | 0 | 3 | 660 | 108 | 3 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 84.8 | 8720 | 42.1 | 3919.5 | -1080 | 5520 | 6600 | 10 | 85.7407 | 5156.65 | 0 | 363.35 | 0 |  | 76.3889 | 6600
25 | 410 | 25 | 435 | 0 | 0 | 3 | 435 | 89 | 8.55 | 0.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.8 | 8720 | 41.9 | 3685.5 | 0 | 6148.8191 | 4393.5 | 10.1 | 84.8917 | 5752.8 | 1755.3191 | 456.0191 | 60 |  | 50.8507 | 4393.5
26 | 210 | 215 | 425 | 0 | 0 | 3 | 425 | 104 | 3.45 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 26 | 84.7 | 8480 | 42 | 3802.5 | -240 | 5807.8191 | 4292.5 | 10.1 | 85.0905 | 5577.2 | 1755.3191 | 290.6191 | 60 |  | 49.6817 | 4292.5
27 | 445 | 170 | 615 | 0 | 0 | 2 | 615 | 108 | 9.5 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0 | 3 | 2 | ΒΛΑΒΗ ΒΑΘΜΙΔΩΝ ΕΚΚΙΝΗΣΗΣ ΜΟΝΑΔΟΣ | 27 | 84.2 | 7280 | 42 | 3802.5 | -1200 | 6181.7128 | 6211.5 | 10.1 | 86.0987 | 5964 | 1170.2128 | 277.7128 | 60 |  | 71.8924 | 6211.5
28 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 55 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.05 | 6920 | 41.65 | 3393 | -360 | 5437.1383 | 4036.5 | 10.35 | 84.3188 | 5299.8 | 1760.6383 | 197.3383 | 60 |  | 46.7188 | 4036.5
29 | 615 | 265 | 880 | 0 | 0 | 3 | 880 | 100 | 12 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.9 | 6560 | 42 | 3802.5 | -360 | 8704 | 9064 | 10.3 | 85.0314 | 8554 | 0 | 210 | 60 |  | 104.9074 | 9064
30 | 240 | 495 | 735 | 0 | 0 | 3 | 735 | 108 | 5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.95 | 6680 | 42 | 3802.5 | 120 | 7543.5 | 7423.5 | 10.1 | 86.6118 | 7497 | 0 | 106.5 | 60 |  | 85.9201 | 7423.5
31 | 155 | 215 | 370 | 0 | 0 | 3 | 370 | 55 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 83.95 | 6680 | 41.7 | 3451.5 | 0 | 3737 | 3737 | 10.1 | 86.6118 | 3628.1 | 0 | 168.9 | 60 |  | 43.2523 | 3737
| 10450 | 11420 | 21870 | 0 | 0 | 91 | 21779 | 110 | 214.63 | 235.03 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0 | 45 | 49 |  |  | 84.2177 | 7322.5806 | 41.9471 | 3740.6032 | -360 | 261141.3063 | 221530.2 | 10.1294 | 85.8127 | 257791.1 | 39971.1063 | 4970.2063 | 1620 |  | 82.7099 | 221530.2