## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 195 | 145 | 340 | 0 | 0 | 3 | 340 | 51 | 4.2 | 3.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.7 | 6080 | 41.66 | 3404.7 | -600 | 3538.1064 | 3553 | 10.45 | 84.2128 | 3516.25 | 585.1064 | 81.8564 | 60 |  | 41.1227 | 3553
2 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 11.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.1 | 7040 | 42.04 | 3849.3 | 960 | 6767.5 | 5807.5 | 10.1 | 86.3032 | 6734 | 0 | 93.5 | 60 |  | 67.2164 | 5807.5
3 | 370 | 0 | 370 | 0 | 0 | 3 | 370 | 55 | 7.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.95 | 9080 | 41.8 | 3568.5 | 2040 | 7095.2128 | 3885 | 10.5 | 81.3726 | 6717.6 | 1170.2128 | 377.6128 | 0 |  | 44.9653 | 3885
4 | 150 | 350 | 500 | 0 | 0 | 3 | 500 | 108 | 2.99 | 7.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 85.1 | 9440 | 41.98 | 3779.1 | 360 | 5410 | 5050 | 10.1 | 84.3008 | 5128.2 | 0 | 281.8 | 0 |  | 58.4491 | 5050
5 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 54 | 8.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.6 | 8240 | 41.84 | 3615.3 | -1200 | 4911.9043 | 3888.5 | 10.1 | 85.2903 | 4686.6 | 2223.4043 | 285.3043 | 60 |  | 45.0058 | 3888.5
6 | 0 | 425 | 425 | 0 | 0 | 3 | 425 | 54 | 0 | 8.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.35 | 7640 | 41.9 | 3685.5 | -600 | 3692.5 | 4292.5 | 10.1 | 85.7938 | 3605 | 0 | 147.5 | 60 |  | 49.6817 | 4292.5
7 | 350 | 150 | 500 | 0 | 0 | 2 | 500 | 100 | 7.2 | 3.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.25 | 7400 | 41.72 | 3474.9 | -240 | 4836.5957 | 5050 | 10.1 | 85.9968 | 4593.7 | 26.5957 | 242.8957 | 0 |  | 58.4491 | 5050
8 | 0 | 340 | 340 | 0 | 0 | 3 | 340 | 55 | 0 | 7.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.75 | 8600 | 41.2 | 2866.5 | 1200 | 6368.0426 | 3434 | 10.1 | 84.991 | 6322 | 1734.0426 | 106.0426 | 60 |  | 39.7454 | 3434
9 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 50 | 8.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.6 | 8240 | 42.05 | 3861 | -360 | 3528.5 | 3888.5 | 10.1 | 85.2903 | 3372.6 | 0 | 215.9 | 60 |  | 45.0058 | 3888.5
10 | 105 | 325 | 430 | 0 | 0 | 3 | 430 | 100 | 2.38 | 7.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 10 | 84.85 | 8840 | 41.98 | 3779.1 | 600 | 4900 | 4300 | 10 | 85.6406 | 4664.7 | 0 | 235.3 | 0 |  | 49.7685 | 4300
11 | 220 | 135 | 355 | 0 | 0 | 3 | 355 | 90 | 5.19 | 3.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.5 | 8000 | 41.98 | 3779.1 | -840 | 3341.2447 | 3585.5 | 10.1 | 85.491 | 3190.1 | 595.7447 | 211.1447 | 60 |  | 41.4988 | 3585.5
12 | 70 | 210 | 280 | 0 | 0 | 3 | 280 | 70 | 1.99 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85.15 | 9560 | 41.85 | 3627 | 1560 | 4388 | 2828 | 10.1 | 84.2032 | 4292.4 | 0 | 95.6 | 0 |  | 32.7315 | 2828
13 | 295 | 90 | 385 | 0 | 0 | 3 | 385 | 80 | 7.05 | 2.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.95 | 9080 | 41.9 | 3685.5 | -480 | 3408.5 | 3888.5 | 10.1 | 84.5953 | 3385.75 | 0 | 82.75 | 60 |  | 45.0058 | 3888.5
14 | 210 | 305 | 515 | 0 | 0 | 3 | 515 | 88 | 5.26 | 7.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 14 | 85.1 | 9440 | 41.9 | 3685.5 | 360 | 6141.2872 | 5201.5 | 10.1 | 84.3008 | 6134.7 | 579.7872 | 66.5872 | 60 |  | 60.2025 | 5201.5
15 | 385 | 190 | 575 | 0 | 0 | 2 | 575 | 110 | 8.15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.95 | 9080 | 41.78 | 3545.1 | -360 | 5390 | 5750 | 10 | 85.4412 | 5277.9 | 0 | 172.1 | 60 |  | 66.5509 | 5750
16 | 120 | 395 | 515 | 0 | 0 | 3 | 515 | 90 | 2.8 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.7 | 8480 | 41.84 | 3615.3 | -600 | 4601.5 | 5201.5 | 10.1 | 85.0905 | 4590.3 | 0 | 71.2 | 60 |  | 60.2025 | 5201.5
17 | 415 | 145 | 560 | 0 | 0 | 3 | 560 | 108 | 8.3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.95 | 9080 | 42.06 | 3872.7 | 600 | 7697.4894 | 5656 | 10.1 | 84.5953 | 7670.5 | 1441.4894 | 86.9894 | 60 |  | 65.463 | 5656
18 | 15 | 255 | 270 | 0 | 0 | 2 | 270 | 100 | 0.4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.05 | 9320 | 41.85 | 3627 | 240 | 7365.9362 | 2727 | 10.1 | 84.3988 | 7307.3 | 4398.9362 | 58.6362 | 0 |  | 31.5625 | 2727
19 | 475 | 50 | 525 | 0 | 0 | 3 | 525 | 90 | 10 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 85.3 | 9920 | 41.99 | 3790.8 | 600 | 5902.5 | 5302.5 | 10.1 | 83.9115 | 5730.5 | 0 | 232 | 60 |  | 61.3715 | 5302.5
20 | 0 | 415 | 415 | 0 | 0 | 3 | 415 | 55 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 20 | 84.25 | 7400 | 42.06 | 3872.7 | -2520 | 5687.629 | 4191.5 | 10.1 | 85.9968 | 5659.2 | 4016.129 | 88.429 | 60 |  | 48.5127 | 4191.5
21 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 54 | 5.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 83.95 | 6680 | 41.19 | 2854.8 | -720 | 4919.2021 | 2777.5 | 10.1 | 86.6118 | 4869.1 | 2861.7021 | 110.1021 | 60 |  | 32.147 | 2777.5
22 | 0 | 245 | 245 | 0 | 0 | 2 | 245 | 54 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.65 | 5960 | 41.47 | 3182.4 | -720 | 5461.4425 | 2609.25 | 10.65 | 82.7306 | 5424.4 | 3572.1925 | 97.0425 | 60 |  | 30.1997 | 2609.25
23 | 280 | 0 | 280 | 0 | 0 | 3 | 280 | 54 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000 | 41.46 | 3170.7 | 2040 | 8437.4468 | 2940 | 10.5 | 82.2342 | 8312.85 | 3457.4468 | 124.5968 | 0 |  | 34.0278 | 2940
24 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 50 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.6 | 8240 | 41.39 | 3088.8 | 240 | 2675.07 | 2435.07 | 10.362 | 83.1338 | 2520 | 0 | 215.07 | 60 |  | 28.1837 | 2435.07
25 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 50 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480 | 41.46 | 3170.7 | 240 | 4633.8776 | 2450 | 10 | 85.9415 | 4462.55 | 1943.8776 | 171.3276 | 0 |  | 28.3565 | 2450
26 | 0 | 275 | 275 | 0 | 0 | 3 | 275 | 50 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8240 | 41.56 | 3287.7 | -240 | 2556.75 | 2796.75 | 10.17 | 84.7032 | 2470.2 | 0 | 146.55 | 60 |  | 32.3698 | 2796.75
27 | 245 | 0 | 245 | 0 | 0 | 2 | 245 | 40 | 6.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.5 | 8000 | 41.9 | 3685.5 | -240 | 2320.25 | 2560.25 | 10.45 | 82.6276 | 2284.9 | 0 | 95.35 | 60 |  | 29.6325 | 2560.25
28 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 40 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.55 | 8120 | 42 | 3802.5 | 120 | 4820.5106 | 2392 | 10.4 | 82.9273 | 4763.25 | 2308.5106 | 117.2606 | 60 |  | 27.6852 | 2392
29 | 300 | 125 | 425 | 0 | 0 | 3 | 425 | 104 | 6.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.7 | 8480 | 41.84 | 3615.3 | 360 | 4652.5 | 4292.5 | 10.1 | 85.0905 | 4674.6 | 0 | 37.9 | 60 |  | 49.6817 | 4292.5
30 | 0 | 230 | 230 | 0 | 0 | 2 | 230 | 55 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360 | 41.61 | 3346.2 | -120 | 2318 | 2438 | 10.6 | 81.1719 | 2173.6 | 0 | 144.4 | 0 |  | 28.2176 | 2438
| 5490 | 5840 | 11330 | 0 | 0 | 84 | 11246 | 110 | 119.2 | 128.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 40 |  |  | 84.6183 | 8284 | 41.7753 | 3539.64 | 1680 | 147767.4978 | 115172.32 | 10.1653 | 84.7063 | 144534.75 | 30915.1778 | 4492.7478 | 1260 |  | 44.4338 | 115172.32