## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 250 | 0 | 250 | 0 | 0 | 3 | 250 | 54 | 5.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.35 | 10040 | 41.6 | 3334.5 | 1680 | 5720.9574 | 2525 | 10.1 | 83.8147 | 5445.8 | 1515.9574 | 275.1574 | 0 |  | 29.2245 | 2525
2 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 50 | 0 | 4.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.35 | 7640 | 41.58 | 3311.1 | -2400 | 4322 | 2222 | 10.1 | 85.7938 | 4267.1 | 4500 | 114.9 | 60 |  | 25.7176 | 2222
3 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 54 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600 | 41.8 | 3568.5 | 960 | 5909 | 4949 | 10.1 | 84.991 | 5765.2 | 0 | 203.8 | 60 |  | 57.2801 | 4949
4 | 0 | 255 | 255 | 0 | 0 | 2 | 255 | 50 | 0 | 5.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.65 | 8360 | 40.46 | 2000.7 | -240 | 2335.5 | 2575.5 | 10.1 | 85.1903 | 2095.1 | 0 | 240.4 | 0 |  | 29.809 | 2575.5
5 | 265 | 25 | 290 | 0 | 0 | 3 | 290 | 70 | 6.32 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 5 | 84.45 | 7880 | 40.67 | 2246.4 | -480 | 5566.0213 | 2929 | 10.1 | 85.5917 | 5526.95 | 3117.0213 | 99.0713 | 60 |  | 33.9005 | 2929
6 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 45 | 0 | 5.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.15 | 7160 | 40.95 | 2574 | -720 | 6722.7766 | 2171.5 | 10.1 | 86.2009 | 6599.2 | 5271.2766 | 183.5766 | 60 |  | 25.1331 | 2171.5
7 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 50 | 4.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.25 | 7400 | 41.03 | 2667.6 | 240 | 4151.3226 | 2121 | 10.1 | 85.9968 | 4157.22 | 1790.3226 | 54.1026 | 60 |  | 24.5486 | 2121
8 | 0 | 165 | 165 | 0 | 0 | 2 | 165 | 45 | 0 | 4.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.2 | 7280 | 40.74 | 2328.3 | -120 | 4850.6965 | 1740.75 | 10.55 | 82.4263 | 4766.4 | 3229.9465 | 144.2965 | 60 |  | 20.1476 | 1740.75
9 | 170 | 0 | 170 | 0 | 0 | 3 | 170 | 50 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 40.5 | 2047.5 | 240 | 5361.2553 | 1717 | 10.1 | 85.8952 | 5212.2 | 3404.2553 | 209.0553 | 60 |  | 19.8727 | 1717
10 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 40 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.2 | 7280 | 40.08 | 1556.1 | -240 | 3335.9468 | 1868.5 | 10.1 | 86.0987 | 3266 | 1707.4468 | 129.9468 | 60 |  | 21.6262 | 1868.5
11 | 260 | 50 | 310 | 0 | 0 | 2 | 310 | 80 | 5.8 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 11 | 84.25 | 7400 | 40 | 1462.5 | 120 | 4304.7634 | 3131 | 10.1 | 85.9968 | 4222.8 | 1053.7634 | 141.9634 | 60 |  | 36.2384 | 3131
12 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 45 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.55 | 8120 | 40.5 | 2047.5 | 720 | 2588.5 | 1868.5 | 10.1 | 85.3905 | 2453.75 | 0 | 134.75 | 0 |  | 21.6262 | 1868.5
13 | 285 | 0 | 285 | 0 | 0 | 3 | 285 | 40 | 6.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.9 | 8960 | 41.46 | 3170.7 | 840 | 3718.5 | 2878.5 | 10.1 | 84.6939 | 3562.4 | 0 | 156.1 | 0 |  | 33.316 | 2878.5
14 | 130 | 220 | 350 | 0 | 0 | 2 | 350 | 108 | 2.62 | 4.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 14 | 85.1 | 9440 | 41.81 | 3580.2 | 480 | 4015 | 3535 | 10.1 | 84.3008 | 3859.1 | 0 | 215.9 | 60 |  | 40.9144 | 3535
15 | 90 | 70 | 160 | 0 | 0 | 3 | 160 | 80 | 2.6 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 85.15 | 9560 | 41.77 | 3533.4 | 120 | 6520.6383 | 1640 | 10.25 | 82.9709 | 6452.5 | 4760.6383 | 128.1383 | 60 |  | 18.9815 | 1640
16 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.8 | 8720 | 41.39 | 3088.8 | -840 | 6574.3191 | 909 | 10.1 | 84.8917 | 6424 | 6505.3191 | 150.3191 | 0 |  | 10.5208 | 909
17 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 40 | 3.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.25 | 9800 | 41.27 | 2948.4 | 1080 | 10302.6383 | 1212 | 10.1 | 84.0085 | 10166.71 | 8010.6383 | 135.9283 | 0 |  | 14.0278 | 1212
18 | 0 | 125 | 125 | 0 | 0 | 2 | 125 | 40 | 0 | 3.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.35 | 10040 | 41.23 | 2901.6 | 240 | 5635.4787 | 1262.5 | 10.1 | 83.8147 | 5652.15 | 4132.9787 | 43.3287 | 60 |  | 14.6123 | 1262.5
19 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 45 | 3.11 | 0 | 0 | 5.83 | 0 | 0 | 0 | 5.83 | 0 | 0 | 1 | 0 | ΣΥΝΤΗΡΗΣΗ Κ.Γ. ΜΕΤΑΦΟΡΑΣ 150KV (ΑΣΩΜΑΤΩΝ - Υ/Σ ΡΑΧΙΑΣ) | 19 | 85.2 | 9680 | 41.24 | 2913.3 | -360 | 6761.5106 | 1313 | 10.1 | 84.1057 | 6578.25 | 5808.5106 | 183.2606 | 0 |  | 15.1968 | 1313
20 | 0 | 130 | 130 | 0 | 0 | 3 | 130 | 50 | 0 | 3.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84 | 6800 | 41.41 | 3112.2 | -2880 | 5379.7979 | 1371.5 | 10.55 | 82.8188 | 5314.25 | 6888.2979 | 125.5479 | 60 |  | 15.8738 | 1371.5
21 | 145 | 0 | 145 | 0 | 0 | 2 | 145 | 54 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.25 | 7400 | 41.64 | 3381.3 | 600 | 2086.25 | 1486.25 | 10.25 | 84.7383 | 1912.6 | 0 | 173.65 | 0 |  | 17.202 | 1486.25
22 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.2 | 7280 | 41.62 | 3357.9 | -120 | 1955.8522 | 1167.25 | 10.15 | 85.6746 | 1830.4 | 908.6022 | 125.4522 | 0 |  | 13.5098 | 1167.25
23 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 41.86 | 3638.7 | 240 | 4807.9787 | 1435 | 10.25 | 84.6382 | 4785 | 3132.9787 | 82.9787 | 60 |  | 16.6088 | 1435
24 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.9 | 6560 | 41.97 | 3767.4 | -960 | 3355.8031 | 2150 | 10 | 87.5823 | 3175.5 | 2165.8031 | 240.3031 | 60 |  | 24.8843 | 2150
25 | 200 | 100 | 300 | 0 | 0 | 3 | 300 | 108 | 4.45 | 2.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.75 | 8600 | 42.05 | 3861 | 2040 | 5070 | 3030 | 10.1 | 84.991 | 4972.8 | 0 | 97.2 | 0 |  | 35.0694 | 3030
26 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85 | 9200 | 41.62 | 3357.9 | 600 | 5464.2487 | 2600 | 10 | 85.3419 | 5146.5 | 2264.2487 | 317.7487 | 0 |  | 30.0926 | 2600
27 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 45 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960 | 41.45 | 3159 | -240 | 2182.0745 | 1262.5 | 10.1 | 84.6939 | 2051.3 | 1159.5745 | 130.7745 | 0 |  | 14.6123 | 1262.5
28 | 90 | 200 | 290 | 0 | 0 | 2 | 290 | 90 | 2.25 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85.25 | 9800 | 41.83 | 3603.6 | 840 | 3740 | 2900 | 10 | 84.8486 | 3586.8 | 0 | 153.2 | 0 |  | 33.5648 | 2900
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.35 | 10040 | 41.48 | 3194.1 | 240 | 5197 | 707 | 10.1 | 83.8147 | 5146.5 | 4250 | 110.5 | 60 |  | 8.1829 | 707
30 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.25 | 7400 | 41.41 | 3112.2 | -2640 | 2191.9681 | 757.5 | 10.1 | 85.9968 | 2073.2 | 4074.4681 | 178.7681 | 60 |  | 8.7674 | 757.5
31 | 160 | 0 | 160 | 0 | 0 | 2 | 160 | 50 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.65 | 8360 | 42.05 | 3861 | 960 | 4404.125 | 1616 | 10.1 | 85.1903 | 4419.22 | 1828.125 | 44.905 | 60 |  | 18.7037 | 1616
| 3330 | 2900 | 6230 | 0 | 0 | 84 | 6146 | 108 | 78.3 | 67.4 | 0 | 5.83 | 0 | 0 | 0 | 5.83 | 0 | 0 | 28 | 26 |  |  | 84.6452 | 8348.3871 | 41.3055 | 2989.9161 | 0 | 144531.9232 | 63051.75 | 10.1207 | 85.026 | 140886.9 | 81480.1732 | 4725.0232 | 1080 |  | 23.5408 | 63051.75