## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 84.5 | 8000 | 41.82 | 3591.9 | -360 | 2144.8723 | 707 | 10.1 | 85.491 | 2109.7 | 1797.8723 | 95.1723 | 60 |  | 8.1829 | 707
2 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.6 | 8240 | 41.6 | 3334.5 | 240 | 933 | 693 | 9.9 | 87.0133 | 667.5 | 0 | 265.5 | 0 |  | 8.0208 | 693
3 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 55 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.65 | 8360 | 41.85 | 3627 | 120 | 4485.898 | 2121 | 10.1 | 85.1903 | 4506.6 | 2244.898 | 9.298 | 30 |  | 24.5486 | 2121
4 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.65 | 8360 | 41.32 | 3006.9 | 0 | 791.25 | 791.25 | 10.55 | 81.5566 | 686 | 0 | 165.25 | 60 |  | 9.158 | 791.25
5 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.2 | 9680 | 40.85 | 2457 | 1320 | 3969.4949 | 700 | 10 | 84.9468 | 3820.3 | 1949.4949 | 149.1949 | 0 |  | 8.1019 | 700
6 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 35 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.1 | 9440 | 40.92 | 2538.9 | -240 | 4851.8421 | 1155 | 10.5 | 81.0894 | 4737.7 | 3936.8421 | 114.1421 | 0 |  | 13.3681 | 1155
7 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 40 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.2 | 7280 | 40.92 | 2538.9 | -2160 | 1037.0417 | 858.5 | 10.1 | 86.0987 | 678.9 | 2338.5417 | 358.1417 | 0 |  | 9.9363 | 858.5
8 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 3.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.95 | 6680 | 41.53 | 3252.6 | -600 | 1997.3511 | 1666.5 | 10.1 | 86.6118 | 1966.25 | 930.8511 | 91.1011 | 60 |  | 19.2882 | 1666.5
9 | 265 | 0 | 265 | 0 | 0 | 2 | 265 | 45 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 84.1 | 7040 | 41.94 | 3732.3 | 360 | 3036.5 | 2676.5 | 10.1 | 86.3032 | 2940 | 0 | 156.5 | 60 |  | 30.978 | 2676.5
10 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 54 | 0 | 3.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.95 | 6680 | 41.6 | 3334.5 | -360 | 1315.575 | 1675.575 | 10.155 | 86.1427 | 1057.9 | 0 | 257.675 | 0 |  | 19.3932 | 1675.575
11 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 45 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.1 | 9440 | 41.84 | 3615.3 | 2760 | 4982 | 2222 | 10.1 | 84.3008 | 4847 | 0 | 135 | 0 |  | 25.7176 | 2222
12 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 85.25 | 9800 | 41.64 | 3381.3 | 360 | 2793.0319 | 757.5 | 10.1 | 84.0085 | 2764.8 | 1675.5319 | 88.2319 | 60 |  | 8.7674 | 757.5
13 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000 | 41.75 | 3510 | -1800 | 3126.9468 | 1969.5 | 10.1 | 85.491 | 3080.6 | 2957.4468 | 106.3468 | 60 |  | 22.7951 | 1969.5
14 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 50 | 0 | 3.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.2 | 7280 | 41.79 | 3556.8 | -720 | 845.5 | 1565.5 | 10.1 | 86.0987 | 700.8 | 0 | 204.7 | 60 |  | 18.1192 | 1565.5
15 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 54 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.05 | 6920 | 41.84 | 3615.3 | -360 | 2973 | 3333 | 10.1 | 86.4059 | 2869 | 0 | 104 | 0 |  | 38.5764 | 3333
16 | 0 | 200 | 200 | 0 | 0 | 2 | 200 | 40 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 16 | 84.5 | 8000 | 41.56 | 3287.7 | 1080 | 3080 | 2000 | 10 | 86.3459 | 2890.8 | 0 | 189.2 | 0 |  | 23.1481 | 2000
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 1.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.7 | 6080 | 41.29 | 2971.8 | -1920 | 922.8723 | 795 | 10.6 | 83.0211 | 751.9 | 2047.8723 | 170.9723 | 0 |  | 9.2014 | 795
18 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.3 | 7520 | 41.28 | 2960.1 | 1440 | 2140 | 700 | 10 | 86.7541 | 2048.75 | 0 | 91.25 | 0 |  | 8.1019 | 700
19 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 1.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000 | 41.25 | 2925 | 480 | 3782.3298 | 738.5 | 10.55 | 81.8444 | 3686.5 | 2563.8298 | 95.8298 | 0 |  | 8.5475 | 738.5
20 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.15 | 9560 | 39.78 | 1205.1 | 1560 | 7604.5933 | 2070.5 | 10.1 | 84.2032 | 7482.5 | 3974.0933 | 122.0933 | 0 |  | 23.9641 | 2070.5
21 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 40 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.8 | 8720 | 39.61 | 1006.2 | -840 | 2335.7564 | 1565.5 | 10.1 | 84.8917 | 2264.8 | 1610.2564 | 130.9564 | 60 |  | 18.1192 | 1565.5
22 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 50 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.05 | 9320 | 40.96 | 2585.7 | 600 | 3449.5957 | 2323 | 10.1 | 84.3988 | 3181.15 | 526.5957 | 268.4457 | 0 |  | 26.8866 | 2323
23 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 50 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.55 | 8120 | 42.03 | 3837.6 | -1200 | 4660.6192 | 2171.5 | 10.1 | 85.3905 | 4547.9 | 3689.1192 | 112.7192 | 0 |  | 25.1331 | 2171.5
24 | 45 | 95 | 140 | 0 | 0 | 2 | 140 | 95 | 0.85 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.3 | 7520 | 41.88 | 3662.1 | -600 | 814 | 1414 | 10.1 | 85.8952 | 729.6 | 0 | 84.4 | 0 |  | 16.3657 | 1414
25 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.9 | 6560 | 41.48 | 3194.1 | -960 | 2988.9583 | 787.5 | 10.5 | 83.4118 | 2759.4 | 3161.4583 | 229.5583 | 0 |  | 9.1146 | 787.5
26 | 170 | 135 | 305 | 0 | 0 | 3 | 305 | 80 | 4.55 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.65 | 8360 | 41.87 | 3650.4 | 1800 | 5486.8421 | 3050 | 10 | 86.0422 | 5431.2 | 636.8421 | 55.6421 | 0 |  | 35.3009 | 3050
27 | 80 | 55 | 135 | 0 | 0 | 3 | 135 | 80 | 2.05 | 1.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.8 | 8720 | 41.79 | 3556.8 | 360 | 7670.3085 | 1363.5 | 10.1 | 84.8917 | 7519 | 5946.8085 | 211.3085 | 60 |  | 15.7812 | 1363.5
28 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 54 | 0 | 5.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.15 | 9560 | 41.91 | 3697.2 | 840 | 6008.4255 | 2828 | 10.1 | 84.2032 | 5767 | 2340.4255 | 241.4255 | 0 |  | 32.7315 | 2828
29 | 465 | 550 | 1015 | 0 | 0 | 3 | 1015 | 108 | 9.3 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.9 | 6560 | 41.77 | 3533.4 | -3000 | 10198.3085 | 10251.5 | 10.1 | 86.7152 | 10074 | 2946.8085 | 184.3085 | 60 |  | 118.6516 | 10251.5
30 | 145 | 715 | 860 | 0 | 0 | 3 | 860 | 110 | 3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.8 | 8720 | 41.65 | 3393 | 2160 | 13122.0417 | 8686 | 10.1 | 84.8917 | 13005 | 2276.0417 | 177.0417 | 60 |  | 100.5324 | 8686
| 3015 | 3275 | 6290 | 0 | 0 | 84 | 6206 | 110 | 69.7 | 72.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 |  |  | 84.535 | 8084 | 41.444 | 3151.98 | 360 | 113547.9552 | 63636.325 | 10.1171 | 85.2766 | 109572.55 | 49551.6302 | 4665.4052 | 690 |  | 24.5511 | 63636.325