## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 45 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.35 | 7640 | 41.63 | 3369.6 | -1080 | 4351.8617 | 1942.5 | 10.5 | 82.5254 | 3606.2 | 3489.3617 | 745.6617 | 0 |  | 22.4826 | 1942.5
2 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.75 | 8600 | 41.34 | 3030.3 | 960 | 2360.9005 | 798.75 | 10.65 | 80.6018 | 2156 | 602.1505 | 264.9005 | 60 |  | 9.2448 | 798.75
3 | 205 | 0 | 205 | 0 | 0 | 2 | 205 | 55 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880 | 42.03 | 3837.6 | -720 | 4176.141 | 2070.5 | 10.1 | 85.5917 | 4164.55 | 2825.641 | 71.591 | 60 |  | 23.9641 | 2070.5
4 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 40 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85 | 9200 | 42.08 | 3896.1 | 1320 | 4151.7766 | 1060.5 | 10.1 | 84.4969 | 4095.3 | 1771.2766 | 116.4766 | 60 |  | 12.2743 | 1060.5
5 | 290 | 210 | 500 | 0 | 0 | 3 | 500 | 100 | 5.9 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.45 | 7880 | 41.77 | 3533.4 | -1320 | 5926.8085 | 5050 | 10.1 | 85.5917 | 5613.7 | 2196.8085 | 313.1085 | 0 |  | 58.4491 | 5050
6 | 0 | 315 | 315 | 0 | 0 | 3 | 315 | 40 | 0 | 8.05 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 6 | 85.3 | 9920 | 41.51 | 3229.2 | 2040 | 6998.5106 | 3150 | 10 | 84.7506 | 6694.1 | 1808.5106 | 304.4106 | 0 |  | 36.4583 | 3150
7 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 50 | 3.55 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 7 | 85.3 | 9920 | 41.83 | 3603.6 | 0 | 5278.1383 | 1767.5 | 10.1 | 83.9115 | 5204.3 | 3510.6383 | 133.8383 | 60 |  | 20.4572 | 1767.5
8 | 155 | 700 | 855 | 0 | 0 | 3 | 855 | 80 | 4.15 | 15.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.8 | 8720 | 41.71 | 3463.2 | -1200 | 9662.5 | 8550 | 10 | 85.7407 | 9555.7 | 2312.5 | 106.8 | 0 |  | 98.9583 | 8550
9 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.5 | 8000 | 41.79 | 3556.8 | -720 | 1042.5638 | 1161.5 | 10.1 | 85.491 | 686.2 | 601.0638 | 416.3638 | 60 |  | 13.4433 | 1161.5
10 | 0 | 80 | 80 | 0 | 0 | 2 | 80 | 40 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84 | 6800 | 41.95 | 3744 | -1200 | 1668.6486 | 820 | 10.25 | 85.2427 | 1638 | 2048.6486 | 90.6486 | 60 |  | 9.4907 | 820
11 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 40 | 0 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 84.15 | 7160 | 41.55 | 3276 | 360 | 4254.3974 | 858.5 | 10.1 | 86.2009 | 3988.6 | 3035.8974 | 265.7974 | 0 |  | 9.9363 | 858.5
12 | 90 | 525 | 615 | 0 | 0 | 3 | 615 | 108 | 1.75 | 9.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 84.55 | 8120 | 41.9 | 3685.5 | 960 | 10543.8404 | 6211.5 | 10.1 | 85.3905 | 10300.05 | 3372.3404 | 303.7904 | 60 |  | 71.8924 | 6211.5
13 | 150 | 420 | 570 | 0 | 0 | 3 | 570 | 110 | 2.75 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 13 | 84.6 | 8240 | 41.62 | 3357.9 | 120 | 12116.2742 | 5899.5 | 10.35 | 83.2301 | 12147.85 | 6096.7742 | 28.4242 | 60 |  | 68.2812 | 5899.5
14 | 0 | 160 | 160 | 0 | 0 | 2 | 160 | 40 | 0 | 4.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85 | 9200 | 41.5 | 3217.5 | 960 | 2560 | 1600 | 10 | 85.3419 | 2138.85 | 0 | 421.15 | 0 |  | 18.5185 | 1600
15 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 1.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 83.7 | 6080 | 41.33 | 3018.6 | -3120 | 2632.0946 | 757.5 | 10.1 | 87.1311 | 2591.5 | 4994.5946 | 100.5946 | 60 |  | 8.7674 | 757.5
16 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 45 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.4 | 7760 | 41.33 | 3018.6 | 1680 | 4049.1383 | 858.5 | 10.1 | 85.6926 | 3892 | 1510.6383 | 217.1383 | 60 |  | 9.9363 | 858.5
17 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 84.8 | 8720 | 41.6 | 3334.5 | 960 | 3853.9362 | 995 | 9.95 | 86.1715 | 3723 | 1898.9362 | 160.9362 | 30 |  | 11.5162 | 995
18 | 0 | 295 | 295 | 0 | 0 | 2 | 295 | 55 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.15 | 7160 | 41.8 | 3568.5 | -1560 | 2749.2872 | 2979.5 | 10.1 | 86.2009 | 2540.4 | 1329.7872 | 208.8872 | 0 |  | 34.485 | 2979.5
19 | 0 | 195 | 195 | 0 | 0 | 3 | 195 | 40 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 85 | 9200 | 41.8 | 3568.5 | 2040 | 8479.1645 | 1998.75 | 10.25 | 83.2604 | 8227.1 | 4440.4145 | 252.0645 | 0 |  | 23.1337 | 1998.75
20 | 40 | 225 | 265 | 0 | 0 | 3 | 265 | 80 | 0.9 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.85 | 8840 | 41.82 | 3591.9 | -360 | 5186.2917 | 2676.5 | 10.1 | 84.7927 | 4978.6 | 2869.7917 | 207.6917 | 0 |  | 30.978 | 2676.5
21 | 170 | 0 | 170 | 0 | 0 | 3 | 170 | 54 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.8 | 8720 | 41.72 | 3474.9 | -120 | 4762.8031 | 1717 | 10.1 | 84.8917 | 4652.55 | 3165.8031 | 170.2531 | 60 |  | 19.8727 | 1717
22 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.85 | 8840 | 41.43 | 3135.6 | 120 | 1412.1064 | 707 | 10.1 | 84.7927 | 1270.2 | 585.1064 | 201.9064 | 60 |  | 8.1829 | 707
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.1 | 9440 | 41.47 | 3182.4 | 600 | 4410.6277 | 858.5 | 10.1 | 84.3008 | 4248.6 | 2952.1277 | 162.0277 | 0 |  | 9.9363 | 858.5
24 | 0 | 150 | 150 | 0 | 0 | 3 | 150 | 45 | 0 | 3.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.7 | 8480 | 42.08 | 3896.1 | -960 | 3528.1183 | 1515 | 10.1 | 85.0905 | 3457.7 | 2973.1183 | 130.4183 | 60 |  | 17.5347 | 1515
25 | 165 | 0 | 165 | 0 | 0 | 2 | 165 | 55 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680 | 41.88 | 3662.1 | 1200 | 6329.266 | 1666.5 | 10.1 | 84.1057 | 6175.8 | 3462.766 | 153.466 | 0 |  | 19.2882 | 1666.5
26 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.5 | 8000 | 41.63 | 3369.6 | -1680 | 3713.1064 | 808 | 10.1 | 85.491 | 3699.1 | 4585.1064 | 74.0064 | 60 |  | 9.3519 | 808
27 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.75 | 6200 | 41.62 | 3357.9 | -1800 | 4891.0638 | 840 | 10.5 | 83.7114 | 4822.2 | 5851.0638 | 128.8638 | 60 |  | 9.7222 | 840
28 | 100 | 190 | 290 | 0 | 0 | 3 | 290 | 110 | 2.05 | 4.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85.05 | 9320 | 41.78 | 3545.1 | 3120 | 6020 | 2900 | 10 | 85.2427 | 5811 | 0 | 209 | 0 |  | 33.5648 | 2900
29 | 75 | 195 | 270 | 0 | 0 | 3 | 270 | 55 | 2 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.25 | 7400 | 41.63 | 3369.6 | -1920 | 807 | 2727 | 10.1 | 85.9968 | 675 | 0 | 132 | 0 |  | 31.5625 | 2727
30 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 50 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360 | 41.61 | 3346.2 | 960 | 2323.5 | 1363.5 | 10.1 | 85.1903 | 2197.3 | 0 | 126.2 | 0 |  | 15.7812 | 1363.5
31 | 260 | 340 | 600 | 0 | 0 | 2 | 600 | 110 | 5.21 | 6.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 31 | 85 | 9200 | 41.71 | 3463.2 | 840 | 6900 | 6060 | 10.1 | 84.4969 | 6667.75 | 0 | 232.25 | 0 |  | 70.1389 | 6060
| 2225 | 4925 | 7150 | 0 | 0 | 87 | 7063 | 110 | 48.31 | 108.37 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 32 |  |  | 84.6435 | 8344.5161 | 41.6919 | 3442.0645 | 480 | 147139.8659 | 72369 | 10.1215 | 85.0219 | 141619.2 | 74290.8659 | 6450.6659 | 930 |  | 27.0195 | 72369