## Φύλλο1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [17 empty] | Peak |  | MW |  | HPP Asomata
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation | [9 empty] | Number of Starts |  |  | Date | Asomata Reservoir Lake |  | Regulating lake (Agia Varvara) |  | Water saved in Asomata Reservoir Lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow | Losses |  | Regulating lake (Agia Varvara)
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | (Change in Asomata Reservoir Content) |  | (same as Total Water to Ag.Varv) |  |  | Production | Pumped upstream |  |  |  | Water from Asomata to Agia Varvara lake
[11 empty] | Unit I | [24 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 | m3 x 1000 |  | m3 x 1000 | q=γ/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9200 | 41.71 | 3197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ (+ζ) | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.7 | 8480 | 41.57 | 3299.4 | -720 | 5673.1064 | 808 | 10.1 | 85.0905 | 5533.4 | 5585.1064 | 199.7064 | 60 |  | 9.3519 | 808
2 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.65 | 5960 | 41.64 | 3381.3 | -2520 | 3725.8421 | 909 | 10.1 | 87.2357 | 3569.7 | 5336.8421 | 216.1421 | 60 |  | 10.5208 | 909
3 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 50 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.55 | 5720 | 41.74 | 3498.3 | -240 | 1628.5 | 1868.5 | 10.1 | 87.4456 | 1620.6 | 0 | 67.9 | 60 |  | 21.6262 | 1868.5
4 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 40 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.95 | 6680 | 41.75 | 3510 | 960 | 3030.5 | 2070.5 | 10.1 | 86.6118 | 2905.4 | 0 | 185.1 | 60 |  | 23.9641 | 2070.5
5 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.2 | 9680 | 42.01 | 3814.2 | 3000 | 8296.5319 | 2121 | 10.1 | 84.1057 | 8139.5 | 3175.5319 | 217.0319 | 60 |  | 24.5486 | 2121
6 | 0 | 100 | 100 | 0 | 0 | 2 | 100 | 35 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.6 | 5840 | 41.52 | 3240.9 | -3840 | 3435.9574 | 1010 | 10.1 | 87.3405 | 3412.8 | 6265.9574 | 83.1574 | 60 |  | 11.6898 | 1010
7 | 145 | 60 | 205 | 0 | 0 | 3 | 205 | 80 | 3.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 85.25 | 9800 | 41.91 | 3697.2 | 3960 | 6010 | 2050 | 10 | 84.8486 | 5868.2 | 0 | 141.8 | 0 |  | 23.7269 | 2050
8 | 85 | 95 | 180 | 0 | 0 | 3 | 180 | 55 | 1.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 85.1 | 9440 | 41.91 | 3697.2 | -360 | 4426.4211 | 1818 | 10.1 | 84.3008 | 4212.1 | 2968.4211 | 214.3211 | 0 |  | 21.0417 | 1818
9 | 340 | 255 | 595 | 0 | 0 | 3 | 595 | 110 | 7.1 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.65 | 8360 | 41.73 | 3486.6 | -1080 | 5995.8265 | 6009.5 | 10.1 | 85.1903 | 5989.8 | 1066.3265 | 66.0265 | 60 |  | 69.5544 | 6009.5
10 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 6.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 |  | 10 | 84.92 | 9008 | 41.73 | 3486.6 | 648 | 3222 | 2574 | 9.9 | 86.3646 | 3022.5 | 0 | 199.5 | 0 |  | 29.7917 | 2574
11 | 95 | 0 | 95 | 0 | 0 | 3 | 95 | 40 | 2.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7640 | 41.48 | 3194.1 | -1368 | 2139.3723 | 959.5 | 10.1 | 85.7938 | 1978.3 | 2547.8723 | 221.0723 | 60 |  | 11.1053 | 959.5
12 | 105 | 235 | 340 | 0 | 0 | 3 | 340 | 100 | 1.96 | 4.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.7 | 8480 | 41.92 | 3708.9 | 840 | 4274 | 3434 | 10.1 | 85.0905 | 4321 | 0 | 3 | 50 |  | 39.7454 | 3434
13 | 185 | 0 | 185 | 0 | 0 | 2 | 185 | 54 | 4.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.9 | 8960 | 41.65 | 3393 | 480 | 2293 | 1813 | 9.8 | 87.2865 | 2197.05 | 0 | 95.95 | 0 |  | 20.9838 | 1813
14 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 55 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.6 | 8240 | 41.83 | 3603.6 | -720 | 4128 | 4848 | 10.1 | 85.2903 | 3737.25 | 0 | 390.75 | 0 |  | 56.1111 | 4848
15 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.35 | 7640 | 41.58 | 3311.1 | -600 | 5822.3936 | 757.5 | 10.1 | 85.7938 | 5785.5 | 5664.8936 | 96.8936 | 60 |  | 8.7674 | 757.5
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.3 | 7520 | 41.07 | 2714.4 | -120 | 2316 | 686 | 9.8 | 88.5246 | 2052 | 1750 | 264 | 0 |  | 7.9398 | 686
17 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480 | 40.74 | 2328.3 | 960 | 8464.8085 | 808 | 10.1 | 85.0905 | 8358.5 | 6696.8085 | 106.3085 | 0 |  | 9.3519 | 808
18 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.9 | 8960 | 40.72 | 2304.9 | 480 | 8134.0899 | 707 | 10.1 | 84.6939 | 8169.12 | 6947.0899 | 24.9699 | 60 |  | 8.1829 | 707
19 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85 | 9200 | 40.78 | 2375.1 | 240 | 9092.7381 | 757.5 | 10.1 | 84.4969 | 9103.1 | 8095.2381 | 49.6381 | 60 |  | 8.7674 | 757.5
20 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 55 | 0 | 5.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.3 | 9920 | 41.89 | 3673.8 | 720 | 8270.5833 | 2373.5 | 10.1 | 83.9115 | 8015.4 | 5177.0833 | 255.1833 | 0 |  | 27.4711 | 2373.5
21 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 1.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000 | 41.79 | 3556.8 | -1920 | 3914.6596 | 707 | 10.1 | 85.491 | 3859.2 | 5127.6596 | 115.4596 | 60 |  | 8.1829 | 707
22 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 1.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.8 | 6320 | 41.72 | 3474.9 | -1680 | 795.5851 | 757.5 | 10.1 | 86.9226 | 671.6 | 1718.0851 | 123.9851 | 0 |  | 8.7674 | 757.5
23 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.6 | 5840 | 41.75 | 3510 | -480 | 2878.5638 | 757.5 | 10.1 | 87.3405 | 2730.2 | 2601.0638 | 148.3638 | 0 |  | 8.7674 | 757.5
24 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.95 | 6680 | 41.37 | 3065.4 | 840 | 1578.75 | 738.75 | 9.85 | 88.8101 | 1337.6 | 0 | 241.15 | 0 |  | 8.5503 | 738.75
25 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.85 | 6440 | 40.93 | 2550.6 | -240 | 2219.6859 | 800 | 10 | 87.687 | 1992.9 | 1659.6859 | 226.7859 | 0 |  | 9.2593 | 800
26 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600 | 40.94 | 2562.3 | 2160 | 2917.5 | 757.5 | 10.1 | 84.991 | 2513.7 | 0 | 463.8 | 60 |  | 8.7674 | 757.5
27 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.95 | 9080 | 40.88 | 2492.1 | 480 | 2291.712 | 707 | 10.1 | 84.5953 | 2087.8 | 1104.712 | 203.912 | 0 |  | 8.1829 | 707
28 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.8 | 8720 | 40.12 | 1602.9 | -360 | 2521.8925 | 812 | 10.15 | 84.4736 | 2550.65 | 2069.8925 | 31.2425 | 60 |  | 9.3981 | 812
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.8 | 8720 | 39.28 | 620.1 | 0 | 2797.4255 | 707 | 10.1 | 84.8917 | 2645.92 | 2090.4255 | 211.5055 | 60 |  | 8.1829 | 707
30 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 2.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.5 | 8000 | 39.67 | 1076.4 | -720 | 2693.2632 | 808 | 10.1 | 85.491 | 2462.4 | 2605.2632 | 230.8632 | 0 |  | 9.3519 | 808
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.9 | 8960 | 40.04 | 1509.3 | 960 | 3525.5957 | 789 | 10.52 | 81.3125 | 3372.6 | 1776.5957 | 212.9957 | 60 |  | 9.1319 | 789
| 2100 | 2540 | 4640 | 0 | 0 | 90 | 4550 | 110 | 50.29 | 58.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 |  |  | 84.5184 | 8044.129 | 41.2794 | 2959.3452 | -240 | 128514.3046 | 46723.75 | 10.0748 | 85.7105 | 124215.79 | 82030.5546 | 5308.5146 | 1010 |  | 17.4446 | 46723.75