## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 55 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200 | 40.58 | 2141.1 | 240 | 6560.2447 | 2474.5 | 10.1 | 84.4969 | 6526.2 | 3845.7447 | 34.0447 | 0 |  | 28.64 | 2474.5
2 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 54 | 0 | 4.42 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 |  | 2 | 84.45 | 7880 | 40.49 | 2035.8 | -1320 | 700 | 2020 | 10.1 | 85.5917 | 657 | 0 | 103 | 60 |  | 23.3796 | 2020
3 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 40 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600 | 40.44 | 1977.3 | 720 | 1982.5 | 1262.5 | 10.1 | 84.991 | 1824.7 | 0 | 217.8 | 60 |  | 14.6123 | 1262.5
4 | 0 | 325 | 325 | 0 | 0 | 2 | 325 | 55 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.15 | 9560 | 40.5 | 2047.5 | 960 | 4242.5 | 3282.5 | 10.1 | 84.2032 | 4175.6 | 0 | 66.9 | 0 |  | 37.9919 | 3282.5
5 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 50 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.35 | 10040 | 40.48 | 2024.1 | 480 | 6867.6596 | 1010 | 10.1 | 83.8147 | 6730.6 | 5377.6596 | 197.0596 | 60 |  | 11.6898 | 1010
6 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 55 | 0 | 4.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85 | 9200 | 40.45 | 1989 | -840 | 1028.5 | 1868.5 | 10.1 | 84.4969 | 685.4 | 0 | 343.1 | 0 |  | 21.6262 | 1868.5
7 | 250 | 265 | 515 | 0 | 0 | 3 | 515 | 110 | 4.65 | 4.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.5 | 8000 | 40.5 | 2047.5 | -1200 | 7214.266 | 5201.5 | 10.1 | 85.491 | 7092 | 3212.766 | 182.266 | 60 |  | 60.2025 | 5201.5
8 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.75 | 8600 | 40.5 | 2047.5 | 600 | 1862.5 | 1262.5 | 10.1 | 84.991 | 1883.4 | 0 | 39.1 | 60 |  | 14.6123 | 1262.5
9 | 240 | 160 | 400 | 0 | 0 | 3 | 400 | 110 | 5.4 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.8 | 8720 | 40.68 | 2258.1 | 120 | 5605.5959 | 4040 | 10.1 | 84.8917 | 5439 | 1445.5959 | 166.5959 | 0 |  | 46.7593 | 4040
10 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.6 | 8240 | 40.43 | 1965.6 | -480 | 3803.5213 | 1666.5 | 10.1 | 85.2903 | 3730.3 | 2617.0213 | 133.2213 | 60 |  | 19.2882 | 1666.5
11 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.25 | 7400 | 40.38 | 1907.1 | -840 | 3691.1842 | 757.5 | 10.1 | 85.9968 | 3715.7 | 3773.6842 | 35.4842 | 60 |  | 8.7674 | 757.5
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.15 | 7160 | 40.48 | 2024.1 | -240 | 5342.5798 | 768.75 | 10.25 | 84.9394 | 5343.25 | 4813.8298 | 59.3298 | 60 |  | 8.8976 | 768.75
13 | 130 | 75 | 205 | 0 | 0 | 3 | 205 | 80 | 3.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85 | 9200 | 40.48 | 2024.1 | 2040 | 6179.6489 | 2070.5 | 10.1 | 84.4969 | 6082.75 | 2069.1489 | 96.8989 | 0 |  | 23.9641 | 2070.5
14 | 44 | 179 | 223 | 0 | 0 | 3 | 223 | 85 | 1.07 | 4.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.3 | 9920 | 40.5 | 2047.5 | 720 | 2950 | 2230 | 10 | 84.7506 | 2708.4 | 0 | 241.6 | 0 |  | 25.8102 | 2230
15 | 110 | 0 | 110 | 0 | 0 | 3 | 110 | 55 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 85.1 | 9440 | 40.5 | 2047.5 | -480 | 5109.7234 | 1111 | 10.1 | 84.3008 | 4964 | 4478.7234 | 205.7234 | 60 |  | 12.8588 | 1111
16 | 206 | 266 | 472 | 0 | 0 | 3 | 472 | 110 | 4.48 | 5.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 85 | 9200 | 40.52 | 2070.9 | -240 | 6316.0851 | 4838 | 10.25 | 83.2604 | 6358.25 | 1718.0851 | 17.8351 | 60 |  | 55.9954 | 4838
17 | 135 | 125 | 260 | 0 | 0 | 3 | 260 | 110 | 3.3 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.3 | 7520 | 40.52 | 2070.9 | -1680 | 3249.6649 | 2626 | 10.1 | 85.8952 | 3139 | 2303.6649 | 170.6649 | 60 |  | 30.3935 | 2626
18 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560 | 40.54 | 2094.3 | -960 | 2192.0946 | 757.5 | 10.1 | 86.7152 | 2219 | 2394.5946 | 33.0946 | 60 |  | 8.7674 | 757.5
19 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.8 | 8720 | 40.49 | 2035.8 | 2160 | 5749.9149 | 808 | 10.1 | 84.8917 | 5416.6 | 2781.9149 | 333.3149 | 0 |  | 9.3519 | 808
20 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 55 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.1 | 9440 | 40.76 | 2351.7 | 720 | 7517.75 | 954 | 10.6 | 80.3244 | 7307.3 | 5843.75 | 210.45 | 0 |  | 11.0417 | 954
21 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 54 | 4.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.15 | 9560 | 40.48 | 2024.1 | 120 | 2089.5 | 1969.5 | 10.1 | 84.2032 | 1927.2 | 0 | 162.3 | 0 |  | 22.7951 | 1969.5
22 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.6 | 8240 | 40.64 | 2211.3 | -1320 | 750.5 | 2070.5 | 10.1 | 85.2903 | 707 | 0 | 103.5 | 60 |  | 23.9641 | 2070.5
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 55 | 2.05 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | ΣΥΝΤΗΡΗΣΗ Υ/Σ 150KV | 23 | 84.9 | 8960 | 40.5 | 2047.5 | 720 | 2130.0464 | 858.5 | 10.1 | 84.6939 | 1969.8 | 551.5464 | 160.2464 | 0 |  | 9.9363 | 858.5
24 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 55 | 0 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.19 | 9656 | 40.5 | 2047.5 | 696 | 3312.3265 | 2050 | 10 | 84.9664 | 3135 | 566.3265 | 177.3265 | 0 |  | 23.7269 | 2050
25 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 55 | 2.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680 | 40.47 | 2012.4 | 24 | 3291.8191 | 1262.5 | 10.1 | 84.1057 | 3131.7 | 2005.3191 | 160.1191 | 0 |  | 14.6123 | 1262.5
26 | 20 | 40 | 60 | 0 | 0 | 3 | 60 | 80 | 0.4 | 0.8 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Η/Κ Απ/Ζ 16 | 26 | 84.3 | 7520 | 40.5 | 2047.5 | -2160 | 5083.5263 | 633 | 10.55 | 82.2314 | 4869.1 | 6610.5263 | 214.4263 | 0 |  | 7.3264 | 633
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.1 | 9440 | 40.17 | 1661.4 | 1920 | 4368.9894 | 757.5 | 10.1 | 84.3008 | 4234 | 1691.4894 | 194.9894 | 60 |  | 8.7674 | 757.5
28 | 110 | 380 | 490 | 0 | 0 | 3 | 490 | 55 | 2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.7 | 8480 | 40.36 | 1883.7 | -960 | 3891 | 4851 | 9.9 | 86.8095 | 3809.7 | 0 | 141.3 | 60 |  | 56.1458 | 4851
| 2350 | 3140 | 5490 | 0 | 0 | 83 | 5407 | 110 | 53.1 | 67.72 | 0 | 13 | 0 | 0 | 0 | 13 | 0 | 0 | 21 | 22 |  |  | 84.7996 | 8719.1429 | 40.4943 | 2040.8143 | -480 | 113083.6409 | 55462.25 | 10.1024 | 84.8722 | 109781.95 | 58101.3909 | 4201.6909 | 900 |  | 22.9259