## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 50 | 0 | 4.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 85.2 | 9680 | 40.68 | 2258.1 | -480 | 8490.5 | 2070.5 | 10.1 | 84.1057 | 8365.8 | 6900 | 184.7 | 60 |  | 23.9641 | 2070.5
2 | 150 | 195 | 345 | 0 | 0 | 4 | 345 | 100 | 4.59 | 5 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 84.8 | 8720 | 41.57 | 3299.4 | -960 | 2524.5 | 3484.5 | 10.1 | 84.8917 | 2540.4 | 0 | 44.1 | 60 |  | 40.3299 | 3484.5
3 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 55 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 85.35 | 10040 | 41.6 | 3334.5 | 1320 | 5501.196 | 2721.6 | 10.08 | 83.981 | 5487 | 1459.596 | 14.196 | 0 |  | 31.5 | 2721.6
4 | 130 | 130 | 260 | 0 | 0 | 3 | 260 | 100 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 85.2 | 9680 | 41.8 | 3568.5 | -360 | 9826.2094 | 2626 | 10.1 | 84.1057 | 9831.95 | 7560.2094 | 54.2594 | 60 |  | 30.3935 | 2626
5 | 135 | 120 | 255 | 0 | 0 | 3 | 255 | 90 | 3.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.3 | 7520 | 41.86 | 3638.7 | -2160 | 9505.9255 | 2575.5 | 10.1 | 85.8952 | 9383.92 | 9090.4255 | 182.0055 | 60 |  | 29.809 | 2575.5
6 | 145 | 145 | 290 | 0 | 0 | 3 | 290 | 108 | 2.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84.9 | 8960 | 41.93 | 3720.6 | 1440 | 11220.1026 | 3016 | 10.4 | 82.2508 | 11263.9 | 6764.1026 | 16.2026 | 60 |  | 34.9074 | 3016
7 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 50 | 7.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.3 | 9920 | 41.82 | 3591.9 | 960 | 6752.6061 | 3232 | 10.1 | 83.9115 | 6505.6 | 2560.6061 | 247.0061 | 0 |  | 37.4074 | 3232
8 | 145 | 180 | 325 | 0 | 0 | 3 | 325 | 55 | 3.05 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.5 | 10400 | 41.8 | 3568.5 | 480 | 5557.3718 | 3282.5 | 10.1 | 83.5257 | 5519.85 | 1794.8718 | 97.5218 | 60 |  | 37.9919 | 3282.5
9 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 50 | 7.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.2 | 9680 | 42 | 3802.5 | -720 | 2880 | 3600 | 10 | 84.9468 | 2779.7 | 0 | 100.3 | 0 |  | 41.6667 | 3600
10 | 210 | 265 | 475 | 0 | 0 | 3 | 475 | 100 | 4.54 | 5.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 85.1 | 9440 | 41.95 | 3744 | -240 | 4510 | 4750 | 10 | 85.1439 | 4216 | 0 | 294 | 0 |  | 54.9769 | 4750
11 | 180 | 165 | 345 | 0 | 0 | 3 | 345 | 90 | 4.01 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84 | 6800 | 42 | 3802.5 | -2640 | 5046.6277 | 3484.5 | 10.1 | 86.5087 | 5026 | 4202.1277 | 80.6277 | 60 |  | 40.3299 | 3484.5
12 | 180 | 180 | 360 | 0 | 0 | 3 | 360 | 100 | 4 | 4.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 85.2 | 9680 | 41.76 | 3521.7 | 2880 | 6480 | 3600 | 10 | 84.9468 | 6324 | 0 | 156 | 0 |  | 41.6667 | 3600
13 | 190 | 190 | 380 | 0 | 0 | 3 | 380 | 100 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.2 | 9680 | 42 | 3802.5 | 0 | 8105.6768 | 3838 | 10.1 | 84.1057 | 8067.75 | 4267.6768 | 97.9268 | 60 |  | 44.4213 | 3838
14 | 210 | 210 | 420 | 0 | 0 | 2 | 420 | 109 | 4.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.45 | 10280 | 42.03 | 3837.6 | 600 | 4842 | 4242 | 10.1 | 83.6218 | 4820.2 | 0 | 21.8 | 0 |  | 49.0972 | 4242
15 | 280 | 310 | 590 | 0 | 0 | 3 | 590 | 110 | 5.7 | 6.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.7 | 8480 | 41.95 | 3744 | -1800 | 4159 | 5959 | 10.1 | 85.0905 | 3607.5 | 0 | 551.5 | 0 |  | 68.9699 | 5959
16 | 155 | 180 | 335 | 0 | 0 | 2 | 335 | 110 | 3.37 | 3.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 85.35 | 10040 | 41.96 | 3755.7 | 1560 | 4943.5 | 3383.5 | 10.1 | 83.8147 | 4468.8 | 0 | 474.7 | 0 |  | 39.1609 | 3383.5
17 | 180 | 180 | 360 | 0 | 0 | 3 | 360 | 90 | 4 | 3.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.55 | 8120 | 41.97 | 3767.4 | -1920 | 4086.9677 | 3636 | 10.1 | 85.3905 | 3862.4 | 2370.9677 | 284.5677 | 60 |  | 42.0833 | 3636
18 | 200 | 195 | 395 | 0 | 0 | 2 | 395 | 100 | 3.98 | 3.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 85.05 | 9320 | 41.99 | 3790.8 | 1200 | 11692.0641 | 3989.5 | 10.1 | 84.3988 | 11695.04 | 6502.5641 | 57.0241 | 60 |  | 46.1748 | 3989.5
19 | 210 | 220 | 430 | 0 | 0 | 3 | 430 | 110 | 4.08 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.4 | 10160 | 41.96 | 3755.7 | 840 | 6854.7172 | 4343 | 10.1 | 83.7181 | 6560.95 | 1671.7172 | 293.7672 | 0 |  | 50.2662 | 4343
20 | 210 | 285 | 495 | 0 | 0 | 2 | 495 | 110 | 4.02 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 85.3 | 9920 | 41.98 | 3779.1 | -240 | 4759.5 | 4999.5 | 10.1 | 83.9115 | 4635.7 | 0 | 153.8 | 30 |  | 57.8646 | 4999.5
21 | 345 | 260 | 605 | 0 | 0 | 3 | 605 | 110 | 6.95 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85.3 | 9920 | 41.95 | 3744 | 0 | 8459.2179 | 6110.5 | 10.1 | 83.9115 | 8167.5 | 2348.7179 | 291.7179 | 0 |  | 70.7234 | 6110.5
22 | 315 | 315 | 630 | 0 | 0 | 3 | 630 | 110 | 6.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 85 | 9200 | 42.05 | 3861 | -720 | 5643 | 6363 | 10.1 | 84.4969 | 5624.75 | 0 | 48.25 | 30 |  | 73.6458 | 6363
23 | 295 | 300 | 595 | 0 | 0 | 3 | 595 | 110 | 5.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 85 | 9200 | 41.84 | 3615.3 | 0 | 6009.5 | 6009.5 | 10.1 | 84.4969 | 5669.6 | 0 | 339.9 | 0 |  | 69.5544 | 6009.5
24 | 240 | 295 | 535 | 0 | 0 | 3 | 535 | 110 | 4.6 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 85.2 | 9680 | 42.07 | 3884.4 | 480 | 7664.1122 | 5403.5 | 10.1 | 84.1057 | 7482.05 | 1780.6122 | 182.0622 | 0 |  | 62.5405 | 5403.5
25 | 215 | 210 | 425 | 0 | 0 | 3 | 425 | 110 | 4.2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 85 | 9200 | 42.02 | 3825.9 | -480 | 7551.8617 | 4292.5 | 10.1 | 84.4969 | 7380.3 | 3739.3617 | 231.5617 | 60 |  | 49.6817 | 4292.5
26 | 235 | 375 | 610 | 0 | 0 | 3 | 610 | 110 | 4.4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.9 | 8960 | 42.01 | 3814.2 | -240 | 6921 | 6161 | 10.1 | 84.6939 | 6712.45 | 1000 | 208.55 | 0 |  | 71.3079 | 6161
27 | 555 | 220 | 775 | 0 | 0 | 4 | 775 | 110 | 11.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.05 | 9320 | 42 | 3802.5 | 360 | 8187.5 | 7827.5 | 10.1 | 84.3988 | 7782.4 | 0 | 405.1 | 0 |  | 90.5961 | 7827.5
28 | 405 | 465 | 870 | 0 | 0 | 3 | 870 | 110 | 9.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85 | 9200 | 41.97 | 3767.4 | -120 | 8667 | 8787 | 10.1 | 84.4969 | 8565 | 0 | 162 | 60 |  | 101.7014 | 8787
29 | 570 | 270 | 840 | 0 | 0 | 3 | 840 | 110 | 11.3 | 5.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 29 | 84.2 | 7280 | 41.83 | 3603.6 | -1920 | 6564 | 8484 | 10.1 | 86.0987 | 6365.6 | 0 | 258.4 | 60 |  | 98.1944 | 8484
30 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 45 | 0 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.3 | 7520 | 41.9 | 3685.5 | 240 | 5593 | 5353 | 10.1 | 85.8952 | 5428.8 | 0 | 224.2 | 60 |  | 61.956 | 5353
| 6765 | 6865 | 13630 | 0 | 0 | 89 | 13541 | 110 | 141.79 | 141.1 | 39.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 30 |  |  | 85 | 9200 | 41.875 | 3656.25 | -2640 | 198998.6567 | 137625.1 | 10.0972 | 84.5202 | 194140.91 | 64013.5567 | 5757.7467 | 900 |  | 53.0961 | 137625.1