## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 505 | 150 | 655 | 0 | 0 | 4 | 655 | 85 | 11.05 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 85.3 | 9920 | 41.95 | 3744 | 2400 | 9015.5 | 6615.5 | 10.1 | 83.9115 | 8627.1 | 0 | 388.4 | 0 |  | 76.5683 | 6615.5
2 | 280 | 585 | 865 | 0 | 0 | 5 | 865 | 110 | 5.15 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 85.35 | 10040 | 41.95 | 3744 | 120 | 11876.9082 | 8736.5 | 10.1 | 83.8147 | 11460 | 3020.4082 | 416.9082 | 0 |  | 101.1169 | 8736.5
3 | 290 | 390 | 680 | 0 | 0 | 4 | 680 | 50 | 5.9 | 9 | 0 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ ΨΥΓΕΙΟΥ ΓΕΝΝΗΤΡΙΑΣ | 3 | 85 | 9200 | 41.82 | 3591.9 | -840 | 6028 | 6868 | 10.1 | 84.4969 | 5798.8 | 0 | 229.2 | 0 |  | 79.4907 | 6868
4 | 175 | 565 | 740 | 0 | 0 | 4 | 740 | 110 | 3.2 | 11.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.95 | 9080 | 41.92 | 3708.9 | -120 | 7354 | 7474 | 10.1 | 84.5953 | 7291.7 | 0 | 122.3 | 60 |  | 86.5046 | 7474
5 | 500 | 190 | 690 | 0 | 0 | 4 | 690 | 100 | 11.05 | 4.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85 | 9200 | 42 | 3802.5 | 120 | 7089 | 6969 | 10.1 | 84.4969 | 6900.3 | 0 | 188.7 | 0 |  | 80.6597 | 6969
6 | 0 | 570 | 570 | 0 | 0 | 4 | 570 | 54 | 0 | 11.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.45 | 10280 | 41.98 | 3779.1 | 1080 | 6723 | 5643 | 9.9 | 85.3111 | 6308.5 | 0 | 414.5 | 0 |  | 65.3125 | 5643
7 | 235 | 315 | 550 | 0 | 0 | 3 | 550 | 75 | 5.05 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 7 | 85.4 | 10160 | 41.75 | 3510 | -120 | 5435 | 5555 | 10.1 | 83.7181 | 5224.4 | 0 | 210.6 | 0 |  | 64.294 | 5555
8 | 0 | 560 | 560 | 0 | 0 | 3 | 560 | 55 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.3 | 9920 | 41.92 | 3708.9 | -240 | 9074.0311 | 5656 | 10.1 | 83.9115 | 8810.85 | 3658.0311 | 323.1811 | 60 |  | 65.463 | 5656
9 | 605 | 300 | 905 | 0 | 0 | 4 | 905 | 108 | 12.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 85.1 | 9440 | 41.81 | 3580.2 | -480 | 8660.5 | 9140.5 | 10.1 | 84.3008 | 8370 | 0 | 290.5 | 0 |  | 105.7928 | 9140.5
10 | 100 | 555 | 655 | 0 | 0 | 3 | 655 | 110 | 2.1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.1 | 9440 | 41.96 | 3755.7 | 0 | 6615.5 | 6615.5 | 10.1 | 84.3008 | 6436.69 | 0 | 178.81 | 0 |  | 76.5683 | 6615.5
11 | 300 | 290 | 590 | 0 | 0 | 3 | 590 | 50 | 6.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.95 | 9080 | 41.89 | 3673.8 | -360 | 5599 | 5959 | 10.1 | 84.5953 | 5347.5 | 0 | 251.5 | 0 |  | 68.9699 | 5959
12 | 145 | 585 | 730 | 0 | 0 | 3 | 730 | 80 | 3.81 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85.05 | 9320 | 41.96 | 3755.7 | 240 | 7613 | 7373 | 10.1 | 84.3988 | 7248.85 | 0 | 364.15 | 0 |  | 85.3356 | 7373
13 | 655 | 40 | 695 | 0 | 0 | 3 | 695 | 75 | 13.77 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480 | 42 | 3802.5 | -840 | 6179.5 | 7019.5 | 10.1 | 85.0905 | 5966.75 | 0 | 212.75 | 0 |  | 81.2442 | 7019.5
14 | 0 | 560 | 560 | 0 | 0 | 3 | 560 | 50 | 0 | 11.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.8 | 8720 | 41.59 | 3322.8 | 240 | 8252.383 | 5656 | 10.1 | 84.8917 | 8051.9 | 2356.383 | 200.483 | 0 |  | 65.463 | 5656
15 | 255 | 305 | 560 | 0 | 0 | 3 | 560 | 55 | 4.82 | 6.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.7 | 8480 | 41.15 | 2808 | -240 | 7756.4255 | 5656 | 10.1 | 85.0905 | 7668 | 2340.4255 | 148.4255 | 60 |  | 65.463 | 5656
16 | 0 | 590 | 590 | 0 | 0 | 3 | 590 | 55 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.9 | 6560 | 40.97 | 2597.4 | -1920 | 7001.3656 | 5959 | 10.1 | 86.7152 | 7041.6 | 2962.3656 | 19.7656 | 60 |  | 68.9699 | 5959
17 | 295 | 310 | 605 | 0 | 0 | 3 | 605 | 54 | 6.33 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85.25 | 9800 | 40.74 | 2328.3 | 3240 | 9350.5 | 6110.5 | 10.1 | 84.0085 | 9139 | 0 | 211.5 | 0 |  | 70.7234 | 6110.5
18 | 75 | 630 | 705 | 0 | 0 | 4 | 705 | 108 | 1.69 | 12.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.1 | 9440 | 41.5 | 3217.5 | -360 | 10143.9197 | 7120.5 | 10.1 | 84.3008 | 10162.3 | 3383.4197 | 41.6197 | 60 |  | 82.4132 | 7120.5
19 | 615 | 0 | 615 | 0 | 0 | 3 | 615 | 55 | 11.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 85.4 | 10160 | 41.32 | 3006.9 | 720 | 10343.8711 | 6211.5 | 10.1 | 83.7181 | 10455 | 3412.3711 | 38.8711 | 150 |  | 71.8924 | 6211.5
20 | 70 | 610 | 680 | 0 | 0 | 3 | 680 | 70 | 1.92 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 85.2 | 9680 | 41.55 | 3276 | -480 | 6320 | 6800 | 10 | 84.9468 | 5978.7 | 0 | 341.3 | 0 |  | 78.7037 | 6800
21 | 570 | 210 | 780 | 0 | 0 | 3 | 780 | 110 | 12.08 | 5.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85 | 9200 | 42.05 | 3861 | -480 | 7320 | 7800 | 10 | 85.3419 | 7212.4 | 0 | 107.6 | 0 |  | 90.2778 | 7800
22 | 80 | 620 | 700 | 0 | 0 | 3 | 700 | 100 | 2.22 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 85.1 | 9440 | 42 | 3802.5 | 240 | 7310 | 7070 | 10.1 | 84.3008 | 7172.5 | 0 | 137.5 | 0 |  | 81.8287 | 7070
23 | 650 | 95 | 745 | 0 | 0 | 3 | 745 | 100 | 13.18 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480 | 42 | 3802.5 | -960 | 11088.3095 | 7524.5 | 10.1 | 85.0905 | 10921.7 | 4523.8095 | 166.6095 | 0 |  | 87.0891 | 7524.5
24 | 95 | 650 | 745 | 0 | 0 | 3 | 745 | 100 | 2.26 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.7 | 8480 | 42 | 3802.5 | 0 | 7524.5 | 7524.5 | 10.1 | 85.0905 | 7300.85 | 0 | 223.65 | 0 |  | 87.0891 | 7524.5
25 | 660 | 0 | 660 | 0 | 0 | 3 | 660 | 54 | 12.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.95 | 9080 | 42 | 3802.5 | 600 | 7200 | 6600 | 10 | 85.4412 | 7060.4 | 0 | 139.6 | 0 |  | 76.3889 | 6600
26 | 170 | 460 | 630 | 0 | 0 | 4 | 630 | 70 | 5.25 | 10.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 26 | 84.8 | 8720 | 42.02 | 3825.9 | -360 | 6003 | 6363 | 10.1 | 84.8917 | 5911.2 | 0 | 151.8 | 60 |  | 73.6458 | 6363
27 | 590 | 75 | 665 | 0 | 0 | 3 | 665 | 100 | 11.85 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.45 | 7880 | 42.11 | 3931.2 | -840 | 8229.1316 | 6716.5 | 10.1 | 85.5917 | 8261.82 | 2352.6316 | 27.3116 | 60 |  | 77.7373 | 6716.5
28 | 200 | 455 | 655 | 0 | 0 | 3 | 655 | 105 | 4 | 9 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 1 | 2 | ΕΡΕΥΝΕΣ ΑΠΟ ΟΜΑΔΑ ΔΙΑΣΩΣΗΣ ΕΜΑΚ ΣΤΗΝ ΛΙΜΝΗ ΑΝΑΡΡΥΘΜΙΣΗΣ | 28 | 83.75 | 6200 | 42.13 | 3954.6 | -1680 | 9595.0745 | 6615.5 | 10.1 | 87.0267 | 9438.9 | 4659.5745 | 156.1745 | 0 |  | 76.5683 | 6615.5
29 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.2 | 9680 | 42 | 3802.5 | 3480 | 11571.0306 | 6514.5 | 10.1 | 84.1057 | 11626.32 | 1576.5306 | 4.7106 | 60 |  | 75.3993 | 6514.5
30 | 0 | 645 | 645 | 0 | 0 | 3 | 645 | 50 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360 | 42.07 | 3884.4 | -1320 | 8673.2234 | 6514.5 | 10.1 | 85.1903 | 8562.9 | 3478.7234 | 110.3234 | 0 |  | 75.3993 | 6514.5
31 | 295 | 375 | 670 | 0 | 0 | 3 | 670 | 55 | 6 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.8 | 8720 | 42.09 | 3907.8 | 360 | 7127 | 6767 | 10.1 | 84.8917 | 7029.9 | 0 | 97.1 | 0 |  | 78.3218 | 6767
| 9055 | 11685 | 20740 | 0 | 0 | 103 | 20637 | 110 | 188.6 | 241 | 0 | 0 | 5.25 | 8 | 0 | 0 | 0 | 8 | 37 | 44 |  |  | 84.9387 | 9052.9032 | 41.8129 | 3583.5968 | 1200 | 248072.6738 | 209148 | 10.0843 | 84.7494 | 242786.83 | 37724.6738 | 5915.8438 | 630 |  | 78.0869 | 209148