## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 640 | 90 | 730 | 0 | 0 | 3 | 730 | 100 | 13.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.75 | 8600 | 42.1 | 3919.5 | -120 | 7253 | 7373 | 10.1 | 84.991 | 7091.04 | 0 | 161.96 | 0 |  | 85.3356 | 7373
2 | 0 | 665 | 665 | 0 | 0 | 5 | 665 | 55 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 85 | 9200 | 41.94 | 3732.3 | 600 | 7316.5 | 6716.5 | 10.1 | 84.4969 | 7181.8 | 0 | 134.7 | 0 |  | 77.7373 | 6716.5
3 | 630 | 130 | 760 | 0 | 0 | 2 | 760 | 95 | 13.15 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 85.15 | 9560 | 42.07 | 3884.4 | 360 | 8036 | 7676 | 10.1 | 84.2032 | 8032.5 | 0 | 23.5 | 20 |  | 88.8426 | 7676
4 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 50 | 0 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.45 | 10280 | 41.86 | 3638.7 | 720 | 7122.5 | 6402.5 | 9.85 | 85.7442 | 6897.5 | 0 | 225 | 0 |  | 74.103 | 6402.5
5 | 525 | 180 | 705 | 0 | 0 | 3 | 705 | 105 | 10.85 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.4 | 10160 | 41.65 | 3393 | -120 | 7000.5 | 7120.5 | 10.1 | 83.7181 | 6960.8 | 0 | 39.7 | 0 |  | 82.4132 | 7120.5
6 | 105 | 590 | 695 | 0 | 0 | 3 | 695 | 110 | 2.05 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.65 | 8360 | 41.7 | 3451.5 | -1800 | 10626.9074 | 7019.5 | 10.1 | 85.1903 | 10582.5 | 5407.4074 | 104.4074 | 60 |  | 81.2442 | 7019.5
7 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 55 | 12.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.2 | 9680 | 41.25 | 2925 | 1320 | 7870 | 6550 | 10 | 84.9468 | 7774.8 | 0 | 95.2 | 0 |  | 75.8102 | 6550
8 | 0 | 620 | 620 | 0 | 0 | 3 | 620 | 55 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.4 | 10160 | 41.02 | 2655.9 | 480 | 10614.3404 | 6262 | 10.1 | 83.7181 | 10547.64 | 3872.3404 | 66.7004 | 0 |  | 72.4769 | 6262
9 | 670 | 155 | 825 | 0 | 0 | 3 | 825 | 108 | 13.15 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.1 | 7040 | 42.05 | 3861 | -3120 | 6844.9324 | 8332.5 | 10.1 | 86.3032 | 6844.56 | 1632.4324 | 60.3724 | 60 |  | 96.441 | 8332.5
10 | 0 | 665 | 665 | 0 | 0 | 4 | 665 | 50 | 0 | 12.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85.4 | 10160 | 41.78 | 3545.1 | 3120 | 9836.5 | 6716.5 | 10.1 | 83.7181 | 9636.8 | 0 | 199.7 | 0 |  | 77.7373 | 6716.5
11 | 690 | 0 | 690 | 0 | 0 | 3 | 690 | 55 | 13.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85.1 | 9440 | 41.79 | 3556.8 | -720 | 9427.9474 | 6969 | 10.1 | 84.3008 | 9280.82 | 3178.9474 | 147.1274 | 0 |  | 80.6597 | 6969
12 | 0 | 625 | 625 | 0 | 0 | 2 | 625 | 54 | 0 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85 | 9200 | 41.93 | 3720.6 | -240 | 8854.4149 | 6312.5 | 10.1 | 84.4969 | 8762.4 | 2781.9149 | 152.0149 | 60 |  | 73.0613 | 6312.5
13 | 612 | 0 | 612 | 0 | 0 | 4 | 612 | 54 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.25 | 9800 | 41.93 | 3720.6 | 600 | 10749.2851 | 6181.2 | 10.1 | 84.0085 | 10533.6 | 3968.0851 | 215.6851 | 0 |  | 71.5417 | 6181.2
14 | 296 | 363 | 659 | 0 | 0 | 2 | 659 | 55 | 6.1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.1 | 9440 | 41.98 | 3779.1 | -360 | 8015.4767 | 6655.9 | 10.1 | 84.3008 | 7965.25 | 1719.5767 | 110.2267 | 60 |  | 77.0359 | 6655.9
15 | 617 | 0 | 617 | 0 | 0 | 3 | 617 | 54 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.3 | 9920 | 41.93 | 3720.6 | 480 | 9259.0684 | 6231.7 | 10.1 | 83.9115 | 9127.95 | 2547.3684 | 131.1184 | 0 |  | 72.1262 | 6231.7
16 | 0 | 640 | 640 | 0 | 0 | 3 | 640 | 54 | 0 | 13.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 85.3 | 9920 | 42.05 | 3861 | 0 | 6400 | 6400 | 10 | 84.7506 | 6304.74 | 0 | 95.26 | 0 |  | 74.0741 | 6400
17 | 644 | 131 | 775 | 0 | 0 | 3 | 775 | 104 | 12.98 | 2.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 17 | 85.1 | 9440 | 42 | 3802.5 | -480 | 7347.5 | 7827.5 | 10.1 | 84.3008 | 7250.4 | 0 | 157.1 | 60 |  | 90.5961 | 7827.5
18 | 0 | 632 | 632 | 0 | 0 | 4 | 632 | 54 | 0 | 12.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.05 | 9320 | 42 | 3802.5 | -120 | 6263.2 | 6383.2 | 10.1 | 84.3988 | 6142.5 | 0 | 150.7 | 30 |  | 73.8796 | 6383.2
19 | 579 | 209 | 788 | 0 | 0 | 3 | 788 | 108 | 12.02 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84.95 | 9080 | 42 | 3802.5 | -240 | 9145.1158 | 7958.8 | 10.1 | 84.5953 | 9035.36 | 1426.3158 | 109.7558 | 0 |  | 92.1157 | 7958.8
20 | 0 | 589 | 589 | 0 | 0 | 3 | 589 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.4 | 10160 | 41.91 | 3697.2 | 1080 | 6822.75 | 5742.75 | 9.75 | 86.7234 | 6706.7 | 0 | 116.05 | 0 |  | 66.467 | 5742.75
21 | 602 | 225 | 827 | 0 | 0 | 3 | 827 | 108 | 11.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.85 | 8840 | 41.9 | 3685.5 | -1320 | 7032.7 | 8352.7 | 10.1 | 84.7927 | 6837.6 | 0 | 195.1 | 0 |  | 96.6748 | 8352.7
22 | 248 | 568 | 816 | 0 | 0 | 3 | 816 | 108 | 5.02 | 10.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.2 | 7280 | 42 | 3802.5 | -1560 | 6681.6 | 8241.6 | 10.1 | 86.0987 | 6772.35 | 0 | 29.25 | 120 |  | 95.3889 | 8241.6
23 | 540 | 184 | 724 | 0 | 0 | 3 | 724 | 108 | 10.1 | 3.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.15 | 9560 | 42.02 | 3825.9 | 2280 | 9592.4 | 7312.4 | 10.1 | 84.2032 | 9337.9 | 0 | 254.5 | 0 |  | 84.6343 | 7312.4
24 | 0 | 564 | 564 | 0 | 0 | 3 | 564 | 54 | 0 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.1 | 9440 | 41.84 | 3615.3 | -120 | 5407.2 | 5527.2 | 9.8 | 86.8815 | 5311.8 | 0 | 95.4 | 0 |  | 63.9722 | 5527.2
25 | 564 | 0 | 564 | 0 | 0 | 3 | 564 | 54 | 11.18 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85.35 | 10040 | 41.75 | 3510 | 600 | 6127.2 | 5527.2 | 9.8 | 86.3804 | 6045 | 0 | 82.2 | 0 |  | 63.9722 | 5527.2
26 | 0 | 559 | 559 | 0 | 0 | 3 | 559 | 54 | 0 | 11.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 85.1 | 9440 | 41.67 | 3416.4 | -600 | 6620.3681 | 5645.9 | 10.1 | 84.3008 | 6437.2 | 1574.4681 | 183.1681 | 0 |  | 65.3461 | 5645.9
27 | 553 | 0 | 553 | 0 | 0 | 3 | 553 | 53 | 11.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.7 | 8480 | 41.74 | 3498.3 | -960 | 6082.7468 | 5585.3 | 10.1 | 85.0905 | 6055.1 | 1457.4468 | 87.6468 | 60 |  | 64.6447 | 5585.3
28 | 478 | 336 | 814 | 0 | 0 | 3 | 814 | 107 | 9.8 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.6 | 8240 | 42 | 3802.5 | -240 | 7981.4 | 8221.4 | 10.1 | 85.2903 | 7873.6 | 0 | 167.8 | 60 |  | 95.1551 | 8221.4
29 | 512 | 0 | 512 | 0 | 0 | 3 | 512 | 50 | 10.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.85 | 8840 | 41.8 | 3568.5 | 600 | 5668.8 | 5068.8 | 9.9 | 86.5057 | 5409.3 | 0 | 259.5 | 0 |  | 58.6667 | 5068.8
30 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 50 | 0 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.4 | 10160 | 41.8 | 3568.5 | 1320 | 6520 | 5200 | 10 | 84.5553 | 6455.75 | 0 | 64.25 | 0 |  | 60.1852 | 5200
31 | 195 | 335 | 530 | 0 | 0 | 3 | 530 | 50 | 4 | 7.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 85.05 | 9320 | 41.93 | 3720.6 | -840 | 4486.5 | 5326.5 | 10.05 | 84.8186 | 4464 | 0 | 22.5 | 0 |  | 61.6493 | 5326.5
| 10355 | 10225 | 20580 | 0 | 0 | 96 | 20484 | 110 | 209.2 | 205.43 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 38 |  |  | 85.0452 | 9308.3871 | 41.8513 | 3628.5097 | 600 | 237006.8535 | 206840.55 | 10.0506 | 84.8234 | 233659.26 | 29566.3035 | 3937.5935 | 590 |  | 77.2254 | 206840.55