## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 330 | 190 | 520 | 0 | 0 | 3 | 520 | 50 | 7.04 | 4.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85.05 | 9320 | 42.09 | 3907.8 | 0 | 5252 | 5252 | 10.1 | 84.3988 | 5328.4 | 0 | 23.6 | 100 |  | 60.787 | 5252
2 | 0 | 480 | 480 | 0 | 0 | 3 | 480 | 50 | 0 | 11.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.2 | 9680 | 42.04 | 3849.3 | 360 | 9727.7895 | 4752 | 9.9 | 85.8048 | 9555.7 | 4615.7895 | 172.0895 | 0 |  | 55 | 4752
3 | 235 | 220 | 455 | 0 | 0 | 3 | 455 | 80 | 5.56 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.9 | 8960 | 42.03 | 3837.6 | -720 | 9141.4574 | 4595.5 | 10.1 | 84.6939 | 9163.5 | 5265.9574 | 37.9574 | 60 |  | 53.1887 | 4595.5
4 | 0 | 465 | 465 | 0 | 0 | 2 | 465 | 45 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 83.75 | 6200 | 42.06 | 3872.7 | -2760 | 5830.117 | 4696.5 | 10.1 | 87.0267 | 5679.4 | 3893.617 | 150.717 | 0 |  | 54.3576 | 4696.5
5 | 455 | 15 | 470 | 0 | 0 | 3 | 470 | 88 | 11.1 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.55 | 8120 | 42.02 | 3825.9 | 1920 | 7772.2632 | 4747 | 10.1 | 85.3905 | 7666.05 | 1105.2632 | 166.2132 | 60 |  | 54.9421 | 4747
6 | 0 | 350 | 350 | 0 | 0 | 3 | 350 | 45 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.4 | 10160 | 41.86 | 3638.7 | 2040 | 5470 | 3430 | 9.8 | 86.2809 | 5175.6 | 0 | 294.4 | 0 |  | 39.6991 | 3430
7 | 268 | 69 | 337 | 0 | 0 | 3 | 337 | 90 | 5.4 | 1.4 | 0 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | ΥΨΗΛΗ ΘΕΡΜΟΚΡΑΣΙΑ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡΑΝΟΥ | 7 | 85.3 | 9920 | 41.82 | 3591.9 | -240 | 3472.2106 | 3403.7 | 10.1 | 83.9115 | 3285 | 308.5106 | 247.2106 | 60 |  | 39.3947 | 3403.7
8 | 182 | 118 | 300 | 0 | 0 | 4 | 300 | 45 | 4.14 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.4 | 10160 | 41.9 | 3685.5 | 240 | 10559.1489 | 3000 | 10 | 84.5553 | 10245.9 | 7319.1489 | 313.2489 | 0 |  | 34.7222 | 3000
9 | 277 | 0 | 277 | 0 | 0 | 3 | 277 | 47 | 6.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.3 | 9920 | 41.8 | 3568.5 | -240 | 6621.5298 | 2797.7 | 10.1 | 83.9115 | 6414.45 | 4063.8298 | 207.0798 | 0 |  | 32.3808 | 2797.7
10 | 0 | 178 | 178 | 0 | 0 | 3 | 178 | 45 | 0 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85.4 | 10160 | 41.18 | 2843.1 | 240 | 9325.034 | 1797.8 | 10.1 | 83.7181 | 9148.6 | 7287.234 | 176.434 | 0 |  | 20.8079 | 1797.8
11 | 294 | 135 | 429 | 0 | 0 | 3 | 429 | 108 | 5.7 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.8 | 8720 | 41.96 | 3755.7 | -1440 | 2892.9 | 4332.9 | 10.1 | 84.8917 | 2795.9 | 0 | 157 | 60 |  | 50.1493 | 4332.9
12 | 0 | 268 | 268 | 0 | 0 | 3 | 268 | 46 | 0 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85 | 9200 | 41.95 | 3744 | 480 | 3759.7167 | 2706.8 | 10.1 | 84.4969 | 3610.8 | 572.9167 | 148.9167 | 0 |  | 31.3287 | 2706.8
13 | 336 | 0 | 336 | 0 | 0 | 2 | 336 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480 | 42.02 | 3825.9 | -720 | 3580.3358 | 3393.6 | 10.1 | 85.0905 | 3388.35 | 906.7358 | 191.9858 | 0 |  | 39.2778 | 3393.6
14 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 53 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.5 | 8000 | 41.95 | 3744 | -480 | 3206.5 | 3686.5 | 10.1 | 85.491 | 2993 | 0 | 213.5 | 0 |  | 42.6678 | 3686.5
15 | 463 | 0 | 463 | 0 | 0 | 4 | 463 | 50 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.8 | 8720 | 41.9 | 3685.5 | 720 | 5396.3 | 4676.3 | 10.1 | 84.8917 | 5200.1 | 0 | 196.2 | 0 |  | 54.1238 | 4676.3
16 | 74 | 447 | 521 | 0 | 0 | 3 | 521 | 108 | 1.5 | 9.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 85.15 | 9560 | 42.07 | 3884.4 | 840 | 7222.5188 | 5262.1 | 10.1 | 84.2032 | 7040.25 | 1120.4188 | 182.2688 | 0 |  | 60.9039 | 5262.1
17 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 54 | 7.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.8 | 8720 | 42 | 3802.5 | -840 | 6580.2105 | 3636 | 10.1 | 84.8917 | 6409.2 | 3784.2105 | 171.0105 | 0 |  | 42.0833 | 3636
18 | 116 | 410 | 526 | 0 | 0 | 3 | 526 | 107 | 2.57 | 8.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.3 | 9920 | 41.86 | 3638.7 | 1200 | 8470.272 | 5312.6 | 10.1 | 83.9115 | 8325 | 1957.672 | 145.272 | 0 |  | 61.4884 | 5312.6
19 | 355 | 195 | 550 | 0 | 0 | 3 | 550 | 102 | 8 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.95 | 9080 | 41.75 | 3510 | -840 | 7715 | 5555 | 10.1 | 84.5953 | 7723.65 | 3000 | 51.35 | 60 |  | 64.294 | 5555
20 | 0 | 444 | 444 | 0 | 0 | 3 | 444 | 53 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960 | 42.05 | 3861 | -120 | 4364.4 | 4484.4 | 10.1 | 84.6939 | 4281.2 | 0 | 83.2 | 0 |  | 51.9028 | 4484.4
21 | 510 | 0 | 510 | 0 | 0 | 3 | 510 | 50 | 12.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.7 | 8480 | 42 | 3802.5 | -480 | 4671 | 5151 | 10.1 | 85.0905 | 4688.75 | 0 | 42.25 | 60 |  | 59.6181 | 5151
22 | 0 | 531 | 531 | 0 | 0 | 3 | 531 | 54 | 0 | 11.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.6 | 8240 | 42 | 3802.5 | -240 | 5783.0404 | 5150.7 | 9.7 | 88.8074 | 5526.1 | 872.3404 | 256.9404 | 0 |  | 59.6146 | 5150.7
23 | 423 | 95 | 518 | 0 | 0 | 3 | 518 | 80 | 10.15 | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.05 | 9320 | 41.9 | 3685.5 | 1080 | 6822.4383 | 5231.8 | 10.1 | 84.3988 | 6852.4 | 510.6383 | 30.0383 | 60 |  | 60.5532 | 5231.8
24 | 40 | 425 | 465 | 0 | 0 | 3 | 465 | 90 | 0.9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.7 | 8480 | 41.98 | 3779.1 | -840 | 4557.4747 | 4650 | 10 | 85.9415 | 4402 | 747.4747 | 155.4747 | 0 |  | 53.8194 | 4650
25 | 342 | 90 | 432 | 0 | 0 | 3 | 432 | 70 | 8.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.6 | 8240 | 41.94 | 3732.3 | -240 | 8979.583 | 4363.2 | 10.1 | 85.2903 | 9018.36 | 4856.383 | 21.223 | 60 |  | 50.5 | 4363.2
26 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 54 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 26 | 84.35 | 7640 | 42.04 | 3849.3 | -600 | 6312.4681 | 3838 | 10.1 | 85.7938 | 6134.6 | 3074.4681 | 177.8681 | 0 |  | 44.4213 | 3838
27 | 400 | 185 | 585 | 0 | 0 | 3 | 585 | 106 | 9.5 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.2 | 7280 | 41.9 | 3685.5 | -360 | 6133.6064 | 5908.5 | 10.1 | 86.0987 | 5950 | 585.1064 | 243.6064 | 60 |  | 68.3854 | 5908.5
28 | 195 | 359 | 554 | 0 | 0 | 3 | 554 | 99 | 4.11 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.7 | 8480 | 41.94 | 3732.3 | 1200 | 8864.5489 | 5595.4 | 10.1 | 85.0905 | 8840.3 | 2069.1489 | 84.2489 | 60 |  | 64.7616 | 5595.4
29 | 251 | 416 | 667 | 0 | 0 | 3 | 667 | 54 | 5.49 | 10.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85 | 9200 | 41.89 | 3673.8 | 720 | 9307.7638 | 6736.7 | 10.1 | 84.4969 | 9277.5 | 1851.0638 | 90.2638 | 60 |  | 77.9711 | 6736.7
30 | 114 | 383 | 497 | 0 | 0 | 3 | 497 | 98 | 2.9 | 8.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.7 | 8480 | 41.85 | 3627 | -720 | 8757.3926 | 5243.35 | 10.55 | 81.4611 | 8822.52 | 4234.0426 | 34.8726 | 100 |  | 60.6869 | 5243.35
| 6020 | 7213 | 13233 | 0 | 0 | 90 | 13143 | 108 | 137 | 161.21 | 0 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 33 | 37 |  |  | 84.8583 | 8860 | 41.925 | 3714.75 | -840 | 196549.0205 | 133387.05 | 10.0799 | 84.9454 | 192942.58 | 64001.9705 | 4466.4405 | 860 |  | 51.4611 | 133387.05