## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 328 | 147 | 475 | 0 | 0 | 3 | 475 | 42 | 8.23 | 4.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.2 | 7280 | 42 | 3802.5 | -1200 | 8788.9894 | 4797.5 | 10.1 | 86.0987 | 8723.5 | 5191.4894 | 125.4894 | 60 |  | 55.5266 | 4797.5
2 | 0 | 419 | 419 | 0 | 0 | 3 | 419 | 54 | 0 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.9 | 8960 | 42 | 3802.5 | 1680 | 7798.8915 | 4315.7 | 10.3 | 83.0493 | 7890 | 1803.1915 | 3.8915 | 95 |  | 49.9502 | 4315.7
3 | 464 | 188 | 652 | 0 | 0 | 3 | 652 | 108 | 9.52 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.95 | 9080 | 40.97 | 2597.4 | 120 | 7673.6211 | 6585.2 | 10.1 | 84.5953 | 7242.8 | 968.4211 | 430.8211 | 0 |  | 76.2176 | 6585.2
4 | 80 | 535 | 615 | 0 | 0 | 3 | 615 | 54 | 2 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.3 | 9920 | 41.91 | 3697.2 | 840 | 9110.0106 | 6211.5 | 10.1 | 83.9115 | 8694.15 | 2058.5106 | 415.8606 | 0 |  | 71.8924 | 6211.5
5 | 273 | 334 | 607 | 0 | 0 | 3 | 607 | 53 | 5.65 | 8.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.9 | 8960 | 41.87 | 3650.4 | -960 | 6340.9128 | 6130.7 | 10.1 | 84.6939 | 6255 | 1170.2128 | 85.9128 | 0 |  | 70.9572 | 6130.7
6 | 400 | 210 | 610 | 0 | 0 | 3 | 610 | 80 | 10 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 85 | 9200 | 41.94 | 3732.3 | 240 | 7250.7409 | 6161 | 10.1 | 84.4969 | 7157.4 | 849.7409 | 93.3409 | 0 |  | 71.3079 | 6161
7 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 50 | 8.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.35 | 10040 | 41.98 | 3779.1 | 840 | 10078.5106 | 3430 | 9.8 | 86.3804 | 9930.85 | 5808.5106 | 147.6606 | 0 |  | 39.6991 | 3430
8 | 89 | 579 | 668 | 0 | 0 | 3 | 668 | 107 | 2.2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 8 | 85.15 | 9560 | 42 | 3802.5 | -480 | 9091.2681 | 6746.8 | 10.1 | 84.2032 | 9022.25 | 2824.4681 | 69.0181 | 0 |  | 78.088 | 6746.8
9 | 0 | 834 | 834 | 0 | 0 | 3 | 834 | 54 | 0 | 18.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 85.2 | 9680 | 41.88 | 3662.1 | 120 | 9656.2205 | 8423.4 | 10.1 | 84.1057 | 9482.8 | 1112.8205 | 173.4205 | 0 |  | 97.4931 | 8423.4
10 | 175 | 683 | 858 | 0 | 0 | 4 | 858 | 108 | 4.05 | 14.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.05 | 9320 | 41.97 | 3767.4 | -360 | 8134.2 | 8494.2 | 9.9 | 86.1038 | 7918 | 0 | 216.2 | 0 |  | 98.3125 | 8494.2
11 | 426 | 531 | 957 | 0 | 0 | 3 | 957 | 100 | 9.4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85.3 | 9920 | 41.97 | 3767.4 | 600 | 10521.1755 | 9330.75 | 9.75 | 86.9237 | 10201.8 | 590.4255 | 319.3755 | 0 |  | 107.9948 | 9330.75
12 | 528 | 331 | 859 | 0 | 0 | 3 | 859 | 107 | 13.1 | 7.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.95 | 9080 | 42 | 3802.5 | -840 | 7750 | 8590 | 10 | 85.4412 | 7518.4 | 0 | 231.6 | 0 |  | 99.4213 | 8590
13 | 892 | 91 | 983 | 0 | 0 | 3 | 983 | 70 | 22.6 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.8 | 8720 | 41.8 | 3568.5 | -360 | 9568.3 | 9928.3 | 10.1 | 84.8917 | 9603.05 | 0 | 25.25 | 60 |  | 114.9109 | 9928.3
14 | 133 | 467 | 600 | 0 | 0 | 3 | 600 | 108 | 2.78 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.8 | 8720 | 41.93 | 3720.6 | 0 | 6060 | 6060 | 10.1 | 84.8917 | 5952 | 0 | 108 | 0 |  | 70.1389 | 6060
15 | 520 | 0 | 520 | 0 | 0 | 3 | 520 | 50 | 12.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.1 | 9440 | 41.89 | 3673.8 | 720 | 5816 | 5096 | 9.8 | 86.8815 | 5727.25 | 0 | 88.75 | 0 |  | 58.9815 | 5096
16 | 497 | 393 | 890 | 0 | 0 | 3 | 890 | 95 | 11.9 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 16 | 84.2 | 7280 | 42 | 3802.5 | -2160 | 6740 | 8900 | 10 | 86.9597 | 6682.5 | 0 | 57.5 | 0 |  | 103.0093 | 8900
17 | 587 | 109 | 696 | 0 | 0 | 3 | 696 | 87 | 12.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.1 | 9440 | 41.3 | 2983.5 | 2160 | 9050.4 | 6890.4 | 9.9 | 86.0039 | 8747.6 | 0 | 302.8 | 0 |  | 79.75 | 6890.4
18 | 0 | 782 | 782 | 0 | 0 | 3 | 782 | 54 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.75 | 8600 | 42 | 3802.5 | -840 | 7058.2 | 7898.2 | 10.1 | 84.991 | 6986.1 | 0 | 72.1 | 0 |  | 91.4144 | 7898.2
19 | 318 | 444 | 762 | 0 | 0 | 3 | 762 | 104 | 7.1 | 10.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.85 | 8840 | 41.9 | 3685.5 | 240 | 7669.5 | 7429.5 | 9.75 | 87.8365 | 7496.2 | 0 | 173.3 | 0 |  | 85.9896 | 7429.5
20 | 470 | 223 | 693 | 0 | 0 | 3 | 693 | 54 | 12 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.9 | 8960 | 41.74 | 3498.3 | 120 | 6911.4 | 6791.4 | 9.8 | 87.2865 | 6710.8 | 0 | 200.6 | 0 |  | 78.6042 | 6791.4
21 | 165 | 321 | 486 | 0 | 0 | 3 | 486 | 50 | 4.1 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.3 | 9920 | 41.9 | 3685.5 | 960 | 10835.7068 | 4860 | 10 | 84.7506 | 10633.8 | 5015.7068 | 201.9068 | 0 |  | 56.25 | 4860
22 | 200 | 311 | 511 | 0 | 0 | 3 | 511 | 107 | 3.75 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 83.2 | 4880 | 41.85 | 3627 | -5040 | 5361.8317 | 5314.4 | 10.4 | 85.6446 | 5369 | 5087.4317 | 52.8317 | 60 |  | 61.5093 | 5314.4
23 | 525 | 298 | 823 | 0 | 0 | 3 | 823 | 108 | 10.55 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 23 | 84.6 | 8240 | 41.87 | 3650.4 | 3360 | 11590 | 8230 | 10 | 86.1432 | 11436.92 | 0 | 153.08 | 0 |  | 95.2546 | 8230
24 | 364 | 270 | 634 | 0 | 0 | 3 | 634 | 108 | 6.37 | 5.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 84.6 | 8240 | 41.9 | 3685.5 | 0 | 6664.4681 | 6340 | 10 | 86.1432 | 6488.75 | 324.4681 | 175.7181 | 0 |  | 73.3796 | 6340
25 | 423 | 159 | 582 | 0 | 0 | 3 | 582 | 54 | 7.93 | 2.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.8 | 8720 | 41.91 | 3697.2 | 480 | 6270.9 | 5790.9 | 9.95 | 86.1715 | 6153.25 | 0 | 117.65 | 0 |  | 67.0243 | 5790.9
26 | 154 | 478 | 632 | 0 | 0 | 3 | 632 | 108 | 3 | 9.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 26 | 84.7 | 8480 | 41.9 | 3685.5 | -240 | 6080 | 6320 | 10 | 85.9415 | 5835.9 | 0 | 244.1 | 0 |  | 73.1481 | 6320
27 | 414 | 96 | 510 | 0 | 0 | 3 | 510 | 108 | 8 | 1.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.3 | 9920 | 41.64 | 3381.3 | 1440 | 6591 | 5151 | 10.1 | 83.9115 | 6510 | 0 | 141 | 60 |  | 59.6181 | 5151
28 | 0 | 244 | 244 | 0 | 0 | 3 | 244 | 50 | 0 | 6.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.95 | 9080 | 41.82 | 3591.9 | -840 | 7977.6596 | 2440 | 10 | 85.4412 | 7908.6 | 6377.6596 | 129.0596 | 60 |  | 28.2407 | 2440
29 | 225 | 0 | 225 | 0 | 0 | 3 | 225 | 54 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760 | 41.84 | 3615.3 | -1320 | 5341.9737 | 2272.5 | 10.1 | 85.6926 | 5120.8 | 4389.4737 | 221.1737 | 0 |  | 26.3021 | 2272.5
30 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 45 | 0 | 2.5 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 30 | 84.2 | 7280 | 41.49 | 3205.8 | -480 | 2327.9362 | 909 | 10.1 | 86.0987 | 2219.2 | 1898.9362 | 108.7362 | 0 |  | 10.5208 | 909
31 | 103 | 0 | 103 | 0 | 0 | 3 | 103 | 35 | 2.94 | 0 | 0 | 14 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 31 | 84.8 | 8720 | 41.63 | 3369.6 | 1440 | 2542.1 | 1102.1 | 10.7 | 80.1315 | 2394 | 0 | 208.1 | 60 |  | 12.7558 | 1102.1
| 9103 | 9567 | 18670 | 0 | 0 | 94 | 18576 | 108 | 205.54 | 205.56 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 37 | 33 |  |  | 84.8258 | 8781.9355 | 41.8323 | 3606.2419 | 240 | 232651.917 | 186940.45 | 10.0129 | 85.5788 | 228012.67 | 45471.467 | 5094.247 | 455 |  | 69.7956 | 186940.45