## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 244 | 99 | 343 | 0 | 0 | 3 | 343 | 96 | 4.86 | 2.1 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 1 | 85.2 | 9680 | 41.9 | 3685.5 | 960 | 6738.7179 | 3430 | 10 | 84.9468 | 6465 | 2348.7179 | 273.7179 | 0 |  | 39.6991 | 3430
2 | 0 | 170 | 170 | 0 | 0 | 3 | 170 | 54 | 0 | 3.4 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 2 | 85.4 | 10160 | 41.74 | 3498.3 | 480 | 6936.3617 | 1717 | 10.1 | 83.7181 | 6909.25 | 4739.3617 | 87.1117 | 60 |  | 19.8727 | 1717
3 | 132 | 68 | 200 | 0 | 0 | 3 | 200 | 70 | 3.16 | 1.99 | 0 | 9 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 3 | 85.2 | 9680 | 41.93 | 3720.6 | -480 | 8709.3122 | 2020 | 10.1 | 84.1057 | 8650.5 | 7169.3122 | 58.8122 | 0 |  | 23.3796 | 2020
4 | 55 | 0 | 55 | 0 | 0 | 3 | 55 | 40 | 1.55 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 4 | 84.6 | 8240 | 41.78 | 3545.1 | -1440 | 9780.9362 | 572 | 10.4 | 82.83 | 9701.01 | 10648.9362 | 139.9262 | 60 |  | 6.6204 | 572
5 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 5 | 84.65 | 8360 | 41.16 | 2819.7 | 120 | 8098.836 | 0 | 10.1 |  | 8110.3 | 7978.836 | 48.536 | 60 |  | 0 | 0
6 | 0 | 216 | 216 | 0 | 0 | 3 | 216 | 54 | 0 | 4.06 | 0 | 6.57 | 0 | 0 | 0 | 6.57 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 6 | 84.9 | 8960 | 41.98 | 3779.1 | 600 | 8942.497 | 2198.88 | 10.18 | 84.0283 | 8913.3 | 6143.617 | 89.197 | 60 |  | 25.45 | 2198.88
7 | 203 | 103 | 306 | 0 | 0 | 3 | 306 | 90 | 4.95 | 2.59 | 0 | 9.5 | 0 | 0 | 0 | 9.5 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 7 | 84.8 | 8720 | 40.83 | 2433.6 | -240 | 2850.6 | 3090.6 | 10.1 | 84.8917 | 2664.5 | 0 | 246.1 | 60 |  | 35.7708 | 3090.6
8 | 121 | 264 | 385 | 0 | 0 | 3 | 385 | 108 | 2.34 | 5.04 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 8 | 84.75 | 8600 | 39.65 | 1053 | -120 | 3768.5 | 3888.5 | 10.1 | 84.991 | 3701.1 | 0 | 67.4 | 0 |  | 45.0058 | 3888.5
9 | 263 | 137 | 400 | 0 | 0 | 3 | 400 | 108 | 5 | 2.62 | 0 | 8.16 | 0 | 0 | 0 | 8.16 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 9 | 84.8 | 8720 | 42.13 | 3954.6 | 120 | 7509.2308 | 4020 | 10.05 | 85.3141 | 7402.2 | 3369.2308 | 107.0308 | 0 |  | 46.5278 | 4020
10 | 84 | 191 | 275 | 0 | 0 | 2 | 275 | 75 | 2.4 | 4.6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 10 | 85.3 | 9920 | 41.86 | 3638.7 | 1200 | 3922.5 | 2722.5 | 9.9 | 85.6066 | 3810 | 0 | 112.5 | 0 |  | 31.5104 | 2722.5
11 | 162 | 0 | 162 | 0 | 0 | 3 | 162 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.4 | 10160 | 41.84 | 3615.3 | 240 | 8455.6872 | 1636.2 | 10.1 | 83.7181 | 8310.4 | 6579.4872 | 145.2872 | 0 |  | 18.9375 | 1636.2
12 | 0 | 207 | 207 | 0 | 0 | 3 | 207 | 54 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.15 | 7160 | 41.88 | 3662.1 | -3000 | 7292.8277 | 2090.7 | 10.1 | 86.2009 | 7293.6 | 8202.1277 | 59.2277 | 60 |  | 24.1979 | 2090.7
13 | 339 | 0 | 339 | 0 | 0 | 3 | 339 | 54 | 7.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000 | 41.84 | 3615.3 | 840 | 12013.9 | 3423.9 | 10.1 | 85.491 | 11950.1 | 7750 | 63.8 | 0 |  | 39.6285 | 3423.9
14 | 0 | 264 | 264 | 0 | 0 | 3 | 264 | 53 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 85.1 | 9440 | 41.76 | 3521.7 | 1440 | 6412.0995 | 2666.4 | 10.1 | 84.3008 | 6313.65 | 2305.6995 | 98.4495 | 0 |  | 30.8611 | 2666.4
15 | 0 | 264 | 264 | 0 | 0 | 3 | 264 | 54 | 0 | 5 | 0 | 0 | 0 | 1.35 | 0 | 0 | 0 | 1.35 | 0 | 1 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Δ/Κ Ρ60 ΡΑΧΙΑΣ | 15 | 84.9 | 8960 | 41.94 | 3732.3 | -480 | 5427.2377 | 2666.4 | 10.1 | 84.6939 | 5197.6 | 3240.8377 | 229.6377 | 0 |  | 30.8611 | 2666.4
16 | 0 | 266 | 266 | 0 | 0 | 3 | 266 | 54 | 0 | 4.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.55 | 8120 | 41.99 | 3790.8 | -840 | 5367.6526 | 2686.6 | 10.1 | 85.3905 | 5226.8 | 3521.0526 | 140.8526 | 0 |  | 31.0949 | 2686.6
17 | 224 | 0 | 224 | 0 | 0 | 3 | 224 | 54 | 4.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.2 | 9680 | 41.84 | 3615.3 | 1560 | 3822.4 | 2262.4 | 10.1 | 84.1057 | 3586.8 | 0 | 235.6 | 0 |  | 26.1852 | 2262.4
18 | 0 | 140 | 140 | 0 | 0 | 3 | 140 | 35 | 0 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.25 | 9800 | 41.91 | 3697.2 | 120 | 7888.8387 | 1414 | 10.1 | 84.0085 | 7854.36 | 6354.8387 | 94.4787 | 60 |  | 16.3657 | 1414
19 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 54 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000 | 41.95 | 3744 | -1800 | 9001.6596 | 2424 | 10.1 | 85.491 | 9008.2 | 8377.6596 | 53.4596 | 60 |  | 28.0556 | 2424
20 | 126 | 232 | 358 | 0 | 0 | 3 | 358 | 100 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.3 | 7520 | 41.86 | 3638.7 | -480 | 5779.417 | 3615.8 | 10.1 | 85.8952 | 5745.6 | 2643.617 | 63.817 | 30 |  | 41.8495 | 3615.8
21 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 54 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000 | 41.95 | 3744 | 480 | 3712 | 3232 | 10.1 | 85.491 | 3547.8 | 0 | 164.2 | 0 |  | 37.4074 | 3232
22 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.9 | 6560 | 41.98 | 3779.1 | -1440 | 2767.7447 | 2862 | 10.6 | 82.6248 | 2750.4 | 1345.7447 | 77.3447 | 60 |  | 33.125 | 2862
23 | 353 | 144 | 497 | 0 | 0 | 4 | 497 | 107 | 8.4 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.55 | 8120 | 41.88 | 3662.1 | 1560 | 6579.7 | 5019.7 | 10.1 | 85.3905 | 6600.7 | 0 | 39 | 60 |  | 58.0984 | 5019.7
24 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.45 | 10280 | 41.9 | 3685.5 | 2160 | 7087.0204 | 2626 | 10.1 | 83.6218 | 6874.6 | 2301.0204 | 212.4204 | 0 |  | 30.3935 | 2626
25 | 113 | 0 | 113 | 0 | 0 | 4 | 113 | 50 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.35 | 10040 | 41.58 | 3311.1 | -240 | 8545.2791 | 1141.3 | 10.1 | 83.8147 | 8515.35 | 7643.9791 | 89.9291 | 60 |  | 13.2095 | 1141.3
26 | 28 | 263 | 291 | 0 | 0 | 3 | 291 | 100 | 0.8 | 6.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.5 | 8000 | 42 | 3802.5 | -2040 | 2515.3162 | 2939.1 | 10.1 | 85.491 | 2474.7 | 1616.2162 | 100.6162 | 60 |  | 34.0174 | 2939.1
27 | 271 | 40 | 311 | 0 | 0 | 3 | 311 | 80 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 85.2 | 9680 | 41.94 | 3732.3 | 1680 | 4821.1 | 3141.1 | 10.1 | 84.1057 | 4680 | 0 | 141.1 | 0 |  | 36.3553 | 3141.1
28 | 0 | 337 | 337 | 0 | 0 | 3 | 337 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.3 | 9920 | 41.97 | 3767.4 | 240 | 10550.4358 | 3403.7 | 10.1 | 83.9115 | 10387.9 | 6906.7358 | 162.5358 | 0 |  | 39.3947 | 3403.7
29 | 277 | 0 | 277 | 0 | 0 | 4 | 277 | 50 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.2 | 9680 | 41.97 | 3767.4 | -240 | 7126.1211 | 2797.7 | 10.1 | 84.1057 | 6963.4 | 4568.4211 | 162.7211 | 0 |  | 32.3808 | 2797.7
30 | 0 | 277 | 277 | 0 | 0 | 3 | 277 | 47 | 0 | 7.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.2 | 9680 | 41.87 | 3650.4 | 0 | 5824.2957 | 2797.7 | 10.1 | 84.1057 | 5807.25 | 3026.5957 | 77.0457 | 60 |  | 32.3808 | 2797.7
| 3555 | 4212 | 7767 | 0 | 0 | 92 | 7675 | 108 | 79.21 | 90.81 | 0 | 79.23 | 0 | 1.35 | 0 | 79.23 | 0 | 1.35 | 20 | 21 |  |  | 84.8867 | 8928 | 41.7603 | 3522.09 | 960 | 198248.2246 | 78506.18 | 10.1077 | 84.656 | 195416.37 | 118782.0446 | 3641.8546 | 810 |  | 30.2879 | 78506.18