## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 216 | 0 | 216 | 0 | 0 | 3 | 216 | 40 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.4 | 10160 | 41.79 | 3556.8 | 480 | 9475.4298 | 2181.6 | 10.1 | 83.7181 | 9405.4 | 6813.8298 | 70.0298 | 0 |  | 25.25 | 2181.6
2 | 0 | 292 | 292 | 0 | 0 | 3 | 292 | 54 | 0 | 6.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.4 | 10160 | 41.88 | 3662.1 | 0 | 6273.6681 | 2949.2 | 10.1 | 83.7181 | 6038.4 | 3324.4681 | 235.2681 | 0 |  | 34.1343 | 2949.2
3 | 146 | 0 | 146 | 0 | 0 | 3 | 146 | 54 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.25 | 9800 | 41.7 | 3451.5 | -360 | 8182.6628 | 1474.6 | 10.1 | 84.0085 | 8015.4 | 7068.0628 | 167.2628 | 0 |  | 17.0671 | 1474.6
4 | 156 | 496 | 652 | 0 | 0 | 3 | 652 | 108 | 2.9 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.2 | 7280 | 41.92 | 3708.9 | -2520 | 4065.2 | 6585.2 | 10.1 | 86.0987 | 3963.9 | 0 | 101.3 | 0 |  | 76.2176 | 6585.2
5 | 0 | 305 | 305 | 0 | 0 | 3 | 305 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.85 | 8840 | 41.91 | 3697.2 | 1560 | 6645.6813 | 3080.5 | 10.1 | 84.7927 | 6432.6 | 2005.1813 | 213.0813 | 0 |  | 35.6539 | 3080.5
6 | 0 | 378 | 378 | 0 | 0 | 4 | 378 | 54 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.25 | 9800 | 41.82 | 3591.9 | 960 | 4740 | 3780 | 10 | 84.8486 | 4605.6 | 0 | 134.4 | 0 |  | 43.75 | 3780
7 | 256 | 47 | 303 | 0 | 0 | 3 | 303 | 107 | 5.13 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 85.35 | 10040 | 41.96 | 3755.7 | 240 | 5157.1795 | 3030 | 10 | 84.6528 | 4886.8 | 1887.1795 | 270.3795 | 0 |  | 35.0694 | 3030
8 | 161 | 313 | 474 | 0 | 0 | 3 | 474 | 108 | 2.87 | 6.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 85.35 | 10040 | 41.92 | 3708.9 | 0 | 5783.6615 | 4645.2 | 9.8 | 86.3804 | 5519.05 | 1138.4615 | 264.6115 | 0 |  | 53.7639 | 4645.2
9 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 54 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.5 | 10400 | 41.94 | 3732.3 | 360 | 4288.7234 | 2450 | 10 | 84.3609 | 4196.85 | 1478.7234 | 91.8734 | 0 |  | 28.3565 | 2450
10 | 0 | 350 | 350 | 0 | 0 | 3 | 350 | 54 | 0 | 7.1 | 0 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ ΜΟΝ Νο Ι | 10 | 85.15 | 9560 | 41.9 | 3685.5 | -840 | 2695 | 3535 | 10.1 | 84.2032 | 2533.1 | 0 | 191.9 | 30 |  | 40.9144 | 3535
11 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 54 | 0 | 8.4 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ ΜΟΝ Νο Ι | 11 | 84.65 | 8360 | 41.9 | 3685.5 | -1200 | 3512.4211 | 4444 | 10.1 | 85.1903 | 3344.25 | 268.4211 | 168.1711 | 0 |  | 51.4352 | 4444
12 | 86 | 205 | 291 | 0 | 0 | 4 | 291 | 70 | 1.95 | 3.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 83.8 | 6320 | 41.6 | 3334.5 | -2040 | 3510.8021 | 2939.1 | 10.1 | 86.9226 | 3445.6 | 2611.7021 | 125.2021 | 60 |  | 34.0174 | 2939.1
13 | 219 | 0 | 219 | 0 | 0 | 3 | 219 | 54 | 4.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.25 | 9800 | 40.65 | 2223 | 3480 | 7635.452 | 2135.25 | 9.75 | 87.0242 | 7470.8 | 2020.202 | 164.652 | 0 |  | 24.7135 | 2135.25
14 | 0 | 250 | 250 | 0 | 0 | 4 | 250 | 54 | 0 | 5.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85.4 | 10160 | 40.23 | 1731.6 | 360 | 9932.8723 | 2525 | 10.1 | 83.7181 | 9900.63 | 7047.8723 | 92.2423 | 60 |  | 29.2245 | 2525
15 | 185 | 65 | 250 | 0 | 0 | 3 | 250 | 108 | 4.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 85.2 | 9680 | 41.22 | 2889.9 | -480 | 4138.2642 | 2525 | 10.1 | 84.1057 | 4056.78 | 2093.2642 | 81.4842 | 0 |  | 29.2245 | 2525
16 | 0 | 226 | 226 | 0 | 0 | 3 | 226 | 54 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.4 | 10160 | 41.26 | 2936.7 | 480 | 6568.8827 | 2282.6 | 10.1 | 83.7181 | 6401.85 | 3806.2827 | 167.0327 | 0 |  | 26.419 | 2282.6
17 | 152 | 0 | 152 | 0 | 0 | 3 | 152 | 54 | 3.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.15 | 9560 | 40.65 | 2223 | -600 | 6068.1787 | 1535.2 | 10.1 | 84.2032 | 5903.37 | 5132.9787 | 164.8087 | 0 |  | 17.7685 | 1535.2
18 | 0 | 271 | 271 | 0 | 0 | 4 | 271 | 54 | 0 | 5.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.95 | 9080 | 40.29 | 1801.8 | -480 | 8778.1526 | 2737.1 | 10.1 | 84.5953 | 8761.2 | 6521.0526 | 76.9526 | 60 |  | 31.6794 | 2737.1
19 | 221 | 167 | 388 | 0 | 0 | 3 | 388 | 107 | 4.57 | 3.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.1 | 9440 | 41.94 | 3732.3 | 360 | 9491.566 | 3918.8 | 10.1 | 84.3008 | 9346.2 | 5212.766 | 145.366 | 0 |  | 45.3565 | 3918.8
20 | 0 | 258 | 258 | 0 | 0 | 3 | 258 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.3 | 9920 | 41.8 | 3568.5 | 480 | 3970.9948 | 2580 | 10 | 84.7506 | 3717.9 | 910.9948 | 253.0948 | 0 |  | 29.8611 | 2580
21 | 263 | 77 | 340 | 0 | 0 | 3 | 340 | 108 | 5.05 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 85.25 | 9800 | 41.84 | 3615.3 | -120 | 3178 | 3298 | 9.7 | 87.4727 | 3014.75 | 0 | 163.25 | 0 |  | 38.1713 | 3298
22 | 0 | 261 | 261 | 0 | 0 | 4 | 261 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.2 | 9680 | 41.86 | 3638.7 | -120 | 10726.6263 | 2636.1 | 10.1 | 84.1057 | 10731 | 8210.5263 | 55.6263 | 60 |  | 30.5104 | 2636.1
23 | 203 | 0 | 203 | 0 | 0 | 3 | 203 | 51 | 5.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.35 | 10040 | 41.56 | 3287.7 | 360 | 7729.4489 | 2050.3 | 10.1 | 83.8147 | 7481.4 | 5319.1489 | 248.0489 | 0 |  | 23.7303 | 2050.3
24 | 0 | 262 | 262 | 0 | 0 | 3 | 262 | 54 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 85.25 | 9800 | 41.65 | 3393 | -240 | 9374.2851 | 2646.2 | 10.1 | 84.0085 | 9390 | 6968.0851 | 44.2851 | 60 |  | 30.6273 | 2646.2
25 | 270 | 0 | 270 | 0 | 0 | 3 | 270 | 54 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.3 | 9920 | 41.94 | 3732.3 | 120 | 9926.7872 | 2727 | 10.1 | 83.9115 | 9908.6 | 7079.7872 | 78.1872 | 60 |  | 31.5625 | 2727
26 | 0 | 203 | 203 | 0 | 0 | 3 | 203 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600 | 41.75 | 3510 | -1320 | 9724.9237 | 2050.3 | 10.1 | 84.991 | 9691.2 | 8994.6237 | 93.7237 | 60 |  | 23.7303 | 2050.3
27 | 244 | 0 | 244 | 0 | 0 | 3 | 244 | 54 | 5.11 | 0 | 0 | 0 | 5.32 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ Μον. Νο Ι | 27 | 84.8 | 8720 | 41.84 | 3615.3 | 120 | 5256.8085 | 2440 | 10 | 85.7407 | 5141.55 | 2696.8085 | 115.2585 | 0 |  | 28.2407 | 2440
28 | 187 | 267 | 454 | 0 | 0 | 4 | 454 | 107 | 3.49 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.9 | 8960 | 41.85 | 3627 | 240 | 8197.7404 | 4585.4 | 10.1 | 84.6939 | 8150.3 | 3372.3404 | 87.4404 | 40 |  | 53.0718 | 4585.4
29 | 257 | 0 | 257 | 0 | 0 | 3 | 257 | 54 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.35 | 10040 | 41.83 | 3603.6 | 1080 | 9165.0617 | 2595.7 | 10.1 | 83.8147 | 9118.8 | 5489.3617 | 106.2617 | 60 |  | 30.0428 | 2595.7
30 | 0 | 329 | 329 | 0 | 0 | 3 | 329 | 54 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.4 | 10160 | 41.9 | 3685.5 | 120 | 4284.7367 | 3322.9 | 10.1 | 83.7181 | 4215.15 | 841.8367 | 69.5867 | 0 |  | 38.4595 | 3322.9
31 | 558 | 57 | 615 | 0 | 0 | 3 | 615 | 108 | 11.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 85.1 | 9440 | 41.78 | 3545.1 | -720 | 5553 | 6273 | 10.2 | 83.4744 | 5590.2 | 0 | 22.8 | 60 |  | 72.6042 | 6273
| 4025 | 5519 | 9544 | 0 | 0 | 99 | 9445 | 108 | 83.65 | 109.54 | 0 | 0 | 38.62 | 0 | 0 | 0 | 0 | 0 | 23 | 29 |  |  | 85.1145 | 9474.8387 | 41.6155 | 3352.6161 | -240 | 204032.2117 | 95958.25 | 10.0543 | 84.6555 | 200378.63 | 108313.9617 | 4263.5817 | 610 |  | 35.8267 | 95958.25